Installing Multiple IF8u Modules on a ControlLogix System

Introduction:

The following procedure details the steps necessary to add multiple IF8u modules to a ControlLogix system.  The following procedure was developed to minimize the amount of labor involved in creating ladder needed for configuring and reading data from the modules.

Procedure:

- Use the existing IF8u sample project found at our website at (www.spectrumcontrols.com) as a starting point.  Make use of the ladder sample directly or copy the tags, user defined data types, module profiles, etc., to your project file.  Be sure to copy the user defined data types as they will be needed to create the configuration and input tags for the module.

- Add the remaining IF8u modules to the IO configuration tree.  Use a sequential naming convention when creating chassis and module names.  The naming convention will be critical when duplicating ladder.  Be sure to include the necessary network bridges on the remote and local racks.  See figure below:

Figure 1

- Duplicate IF8u configuration and input tags as needed for all universal modules in the system.  Use the tag editor in RSLogix 5000 or export the tag database as a CSV file and add the tags using MS Excel.  Refer to the figures below.

Figure 2 (RSLogix 5000 Tag Database)

Copy Tag, paste and change the tag number.

Figure 3A (Excel CSV)

Enter tag name with tag number, drag and add series

Figure 3B (Excel CSV)

Drag and add series

Note:  If you used Excel to add new tags, remember to import the tags back into your project when you’re finished.

- Create a routine under the main task called “Initialize_IF8Us”.
Figure 4

- Create a routine under the main task called “Read_IF8Us”.

Figure 5

- Call the two subroutines from the MainRoutine by using the JSR instruction.

Note:  You may want to add a first scan condition ahead of the JSR for the Initialize_IF8U subroutine because the configuration only needs to be written once to each module.  See figure below:

Figure 6

- Save your project file as a “structured text file”.

- Using the provided Excel spread sheet, run the MACROs to create the ladder code for copying the data from the defined tags to the tags generated automatically when the generic profile for the IF8u module was created.

Note: To create the rungs necessary to copy the configuration data from the user defined tags to the module tags, run the ConfigurationLadder macro by pressing CTRL A.  To create the rungs necessary to copy the input data from the module tags to the user defined tags, run the InputLadder macro by pressing CTRL B.

Note: Each macro will prompt you to enter data.  See figure below.

Figure 7

Figure 8

- Copy and paste the logic generated by the excel spreadsheet into the structured text file created in step 7.

Note:  Please be sure to paste the logic into the correct subroutine.  See figures below.

Figure 9

Figure 10

- Import the structured text file back into RSLogix 5000.

5/25/04

Jeff Robel

Applications Engineer

Spectrum Controls, Inc.

(425) 746-9481