GE 7EA Major Inspection Work-Scope

- Mobilize on job site.

- Inspect turbine while operational for leakage (wrapper and 4-way joints)

- Technical director to obtain per outage performance data (prior to shutdown)

- Visually inspect all Compartments.

- Prepare for and perform a check of unit alignment.

- Check Unit Coupling Alignments.(acc gear to turbine and turbine to generator)

- Remove turbine compartment roof and side panels.

- Remove fuel, steam injection and other ancillary/associated piping.

- Prepare for and disassemble turbine combustion section (fuel nozzles, x-fire tubes and retainers, flow sleeves, combustion liners.

- Perform internal rotor (6-Point) position checks though probe holes..

- Visually inspect, clean and provide checks on all disassembled compressor hardware.

- Prepare for and disassemble inlet air duct section from elbow.

- Visually inspect, clean and provide checks on all disassembled compressor hardware.

- Inspect inlet guide vanes and bushings and correct excessive backlash and end play.

- Visually inspect inlet filter housing, bell mouth and inlet plenum compartment.

- Set centerline jacks and remove upper half casings (inspect and store fasteners)

- Take and record a complete set of turbine-compressor and seal clearances.

- Float rotor and record rotor float (axial movement and record data)

- Disassemble rotors at marriage coupling.

- Prep rotor for removal and store per OEM requirements.

- Inspect bearings for contact pattern with rotor(journals 1-2-3)

- Review with customer (6-point, clearances and bearing contact patters to determine if internal alignment is possible warranted.)

- Remove bearing seals and liners for inspection.

- Remove stage 1–2- 3 nozzles and support ring for inspection-complete inspection data format.

- Based on as found inspection and customers request (stage 1-2-3 shroud blocks may be removed)

- Perform inspection on all casing joints and report degradation observed. (repair as required)

- Inspect accessory gears (complete disassembly required) inspect gears-bearings-shaves

- Prepare for and provide checks on lube oil tanks and associated equipment.

- Disassemble, inspect and re-assemble gas stop ratio valve.

- Identify and resolve G.E. TIL’s for the Unit.

- Based on engineering data reported to customer, customer may elect to perform tops on internal bearing and casing alignment checks. Carry out Bearing & Casing Alignment Checks and correct Alignment.

- Prepare for and perform turbine component reassembly.

- Shroud reassembly if removed and replaced (install new shrouds will require, position-gap setting, remove for drilling pinning – B/S and clr. Holes at local shop and final assembly.

- Installation of stage 1-2-3 nozzles and support ring.

- Installation bearing liners and seals 1-2-3 bearings

- Perform H/J blade drop checks and report findings (install keys as required)

- Install turbine and compressor rotors (install marriage coupling bolting).

- Position and float rotor insure float and A-0set is correct.

- Take and record a complete set of compressor- turbine – seal clearances

- Repair casing leaks prior to reassembly of casings.

- Final inspect all casing machined surfaces prior to reassembly.

- Reassemble casings per OEM torque specifications

- Remove centerline jacks

- Take and record 6-point rotor final clearances

- Install fuel, steam injection and other ancillary lines/associated piping.

- Install turbine compartment roof and side panels.

- Final Inspection of all Compartments.

- Clean job site and prepare the unit for operation.

- Crate used combustion parts in crates provided.

- Leak check all areas of turbine at first operational run.

- Demobilize and move off job site.

- Provide Final Inspection report with in four weeks of outage completion date.