## Essex 9
SYSTEM (#) | EQUIPTMENT ID | SERIAL NUMBER | DESCRIPTION | TAG NUMBER | LOCATION | EQUIPMENT TYPE | MODEL # | MANUFACTURER | MANUFACTURER PART # | P&ID # | CSA ITEM (YES/NO) | MATERIAL | SIZE | FRAME | CYCLE (HZ) | PHASE | VOLTAGE | AMPERAGE | WATTAGE | RPM | HORSEPOWER | FLOW | PSIG | SET POINT
(For Major Equipment)
GAS TURBINE ENGINE (01) | EX-09-1-X-01-01-001 | 295581 | GE MS7001 EA |  | CTG TURBINE COMPARTMENT | CT | MS 7001 EA | GE
GT LUBE OIL | EX-09-1-X-01-05-001 |  | IMMERSION HEATER - LUBE OIL TANK | 23QT-1 | AULILIARY SKID, LUBE OIL TANK | HTR |  |  |  | 355B7032 |  |  |  |  | 60 | 3 | 460 AC |  | 15 KW
GT LUBE OIL | EX-09-1-X-01-05-002 |  | IMMERSION HEATER - LUBE OIL TANK | 23QT-2 | AULILIARY SKID, LUBE OIL TANK | HTR |  |  |  | 355B7032 |  |  |  |  | 60 | 3 | 460 AC |  | 15 KW
GT LUBE OIL | EX-09-1-X-01-05-003 |  | MIST SEPARATOR TANK HEATER | 23QV-1 | AUXILIARY SKID | HTR |  |  |  | 355B7032 |  |  |  |  | 60 | 3 | 460 AC |  | 15 KW
GT LUBE OIL | EX-09-1-X-01-05-004 |  | TEMPERATURE SWITCH - LUBE OIL HEADER HIGH ALARM | 26QA-1 | AUXILIARY SKID | TS |  |  |  | 355B7032 | [13 empty] | 165 DEG. F
GT LUBE OIL | EX-09-1-X-01-05-005 |  | TEMPERATURE SWITCH - LUBE OIL TANK HEATERS ON/OFF | 26QL-1 | AULILIARY SKID, LUBE OIL TANK | TS |  |  |  | 355B7032 | [13 empty] | 70 DEG. F
GT LUBE OIL | EX-09-1-X-01-05-006 |  | TEMPERATURE SWITCH - LUBE OIL TANK NORMAL | 26QN-1 | AULILIARY SKID, LUBE OIL TANK | TS |  |  |  | 355B7032 | [13 empty] | 60 DEG. F
GT LUBE OIL | EX-09-1-X-01-05-007 |  | TEMPERATURE SWITCH - LUBE OIL HEADER HIGH TRIP | 26QT-1A | AUXILIARY SKID | TS |  |  |  | 355B7032 | [13 empty] | 175 DEG. F
GT LUBE OIL | EX-09-1-X-01-05-008 |  | TEMPERATURE SWITCH - LUBE OIL HEADER HIGH TRIP | 26QT-1B | AUXILIARY SKID | TS |  |  |  | 355B7032 | [13 empty] | 175 DEG. F
GT LUBE OIL | EX-09-1-X-01-05-009 |  | THERMOSTAT - MIST SEPARATOR TANK HEATER | 26QV-1 | AUXILIARY SKID | TS |  |  |  | 355B7032 | [13 empty] | 60 DEG. F
GT LUBE OIL | EX-09-1-X-01-05-010 |  | PRESSURE SWITCH - LUBE OIL LOW ALARM | 63QA-1 | AUXILIARY SKID | PS |  |  |  | 355B7032 | [13 empty] | 70 PSIG
GT LUBE OIL | EX-09-1-X-01-05-011 |  | PRESSURE SWITCH - LUBE OIL LOW EMERGENCY PUMP START | 63QL-1 | AUXILIARY SKID | PS |  |  |  | 355B7032 | [13 empty] | 6 PSIG
GT LUBE OIL | EX-09-1-X-01-05-012 |  | PRESSURE SWITCH - LUBE OIL FILTER DIFF PRESSURE ALARM | 63QQ-1 | AUXILIARY SKID | PS |  |  |  | 355B7032 | [13 empty] | 15 PSID
GT LUBE OIL | EX-09-1-X-01-05-013 |  | LEVEL SWITCH - LUBE OIL TANK HIGH ALARM | 71QH-1 | AUXILIARY SKID | LS |  |  |  | 355B7032
GT LUBE OIL | EX-09-1-X-01-05-014 |  | LEVEL SWITCH - LUBE OIL TANK LOW ALARM | 71QL-1 | AUXILIARY SKID | LS |  |  |  | 355B7032
GT LUBE OIL | EX-09-1-X-01-05-015 |  | AUXILIARY LUBE OIL PUMP/MOTOR ASSY | 88QA-1 | AUXILIARY SKID | MOT |  | MOTOR - GE, PUMP - BUFFALO FORGE |  | 355B7032 |  |  |  |  | 60 | 3 | 230/460 AC |  |  | 3600 | 60
GT LUBE OIL | EX-09-1-X-01-05-016 |  | EMERGENCY LUBE OIL PUMP/MOTOR ASSY | 88QE-1 | AUXILIARY SKID | MOT |  | MOTOR - GE, PUMP - BUFFALO FORGE |  | 355B7032 | [6 empty] | 120 DC |  |  | 1750 | 10
GT LUBE OIL | EX-09-1-X-01-05-017 |  | LUBE MIST SEPARATOR MOTOR | 88QV-1 | AUXILIARY SKID | MOT |  | GE |  | 355B7032 |  |  |  |  | 60 | 3 | 460 AC |  |  | 3600 | 7.5
GT LUBE OIL | EX-09-1-X-01-05-018 |  | THERMOCOUPLE - #1 BEARING DRAIN | LT-B1D-A | LUBE OIL DRAIN PIPING | TC |  |  |  | 355B7032
GT LUBE OIL | EX-09-1-X-01-05-019 |  | THERMOCOUPLE - #1 BEARING DRAIN | LT-B1D-B | LUBE OIL DRAIN PIPING | TC |  |  |  | 355B7032
GT LUBE OIL | EX-09-1-X-01-05-020 |  | THERMOCOUPLE - #2 BEARING DRAIN | LT-B2D-A | LUBE OIL DRAIN PIPING | TC |  |  |  | 355B7032
GT LUBE OIL | EX-09-1-X-01-05-021 |  | THERMOCOUPLE - #2 BEARING DRAIN | LT-B2D-B | LUBE OIL DRAIN PIPING | TC |  |  |  | 355B7032
GT LUBE OIL | EX-09-1-X-01-05-022 |  | THERMOCOUPLE - #3 BEARING DRAIN | LT-B3D-A | LUBE OIL DRAIN PIPING | TC |  |  |  | 355B7032
GT LUBE OIL | EX-09-1-X-01-05-023 |  | THERMOCOUPLE - #3 BEARING DRAIN | LT-B3D-B | LUBE OIL DRAIN PIPING | TC |  |  |  | 355B7032
GT LUBE OIL | EX-09-1-X-01-05-024 |  | THERMOCOUPLE - #1 THRUST DRAIN | LT-BT1D-A | LUBE OIL DRAIN PIPING | TC |  |  |  | 355B7032
GT LUBE OIL | EX-09-1-X-01-05-025 |  | THERMOCOUPLE - #1 THRUST DRAIN | LT-BT1D-B | LUBE OIL DRAIN PIPING | TC |  |  |  | 355B7032
GT LUBE OIL | EX-09-1-X-01-05-026 |  | THERMOCOUPLE - LUBE OIL HEADER TEMP | LT-TH-1A | LUBE OIL HEADER PIPING | TC |  |  |  | 355B7032
GT LUBE OIL | EX-09-1-X-01-05-027 |  | THERMOCOUPLE - LUBE OIL HEADER TEMP | LT-TH-1B | LUBE OIL HEADER PIPING | TC |  |  |  | 355B7032
GT LUBE OIL | EX-09-1-X-01-05-028 |  | PRESSURE REGULATOR - LUBE OIL HEADER PRESSURE | VPR2-1 | AUXILIARY SKID | PRG | 525 | MASONEILAN INTERNATIONAL, INC. |  | 355B7032 | [13 empty] | 26 PSIG
GT LUBE OIL | EX-09-1-X-01-05-029 |  | RELIEF VALVE - MAIN LUBE OIL PUMP | VR1-1 | AUXILIARY SKID | PRV | 135 | O.C. KECKLEY CO. |  | 355B7032 | [13 empty] | 101 PSIG
GT LUBE OIL | EX-09-1-X-01-05-030 |  | AUXILIARY LUBE OIL PUMP | P2 | AUXILIARY SKID | PMP |  | BUFFALO FORGE PUMP CO. |  | 355B7032 | [11 empty] | 480 GPM | 100 PSIG
GT LUBE OIL | EX-09-1-X-01-05-031 |  | EMERGENCY LUBE OIL PUMP | P1 | AUXILIARY SKID | PMP | VCRE | BUFFALO FORGE PUMP CO. |  | 355B7032 | [11 empty] | 250 GPM | 30 PSIG
GT LUBE OIL | EX-09-1-X-01-05-032 |  | MAIN LUBE OIL PUMP, SHAFT DRIVEN |  | ACCESSORY GEAR | PMP |  | GE |  | 355B7032 | [11 empty] | 460 GPM | 100 PSIG
GT LUBE OIL | EX-09-1-X-01-05-033 |  | LUBE OIL HEAT EXCHANGER |  | AUXILIARY SKID | HE | TYPE 6 | BASCO DIV/AMERICAN PREC IND |  | 355B7032
GT LUBE OIL | EX-09-1-X-01-05-034 |  | LUBE OIL FILTER |  | AUXILIARY SKID | FLT | F3-9XE | HILLIARD CORP |  | 355B7032
GT LUBE OIL | EX-09-1-X-01-05-035 |  | MIST SEPARATOR |  | AUXILIARY SKID | SEP |  | MONSANTO ENVIRO-CHEM |  | 355B7032
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-001 |  | HYDRAULIC FILTER DIFF PRESS ALARM | 63HF-1 | HYDRAULIC GAUGE PANEL | PS |  |  |  | 355B7029 | [13 empty] | 60 PSID
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-002 |  | HYDRAULIC FILTER DIFF PRESS ALARM | 63HF-2 | HYDRAULIC GAUGE PANEL | PS |  |  |  | 355B7029 | [13 empty] | 60 PSID
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-003 |  | LOW HYDRAULIC SUPPLY PRESSURE - AUX PUMP START | 63HQ-1 | HYDRAULIC GAUGE PANEL | PS |  |  |  | 355B7029 | [13 empty] | 1350 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-004 |  | AUXILIARY HYDRAULIC PUMP/MOTOR ASSY | 88HQ-1 | AUXILIARY SKID | MOT |  | MOTOR - GE, PUMP - HARTMAN CONTROLS |  | 355B7029 |  |  |  |  | 60 | 3 | 460 AC |  |  | 1750 | 15 | 16.5 GPM | 1500 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-005 |  | HYDRAULIC ACCUMULATOR | AH1-1 | AUXILIARY SKID | ACC | 7A20 | HALE FIRE PUMP |  | 355B7029 | [12 empty] | 750 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-006 |  | HYDRAULIC ACCUMULATOR | AH1-2 | AUXILIARY SKID | ACC | 7A20 | HALE FIRE PUMP |  | 355B7029 | [12 empty] | 750 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-007 |  | HYDRAULIC SUPPLY FILTER | FH2-1 | HYDRAULIC FILTER ASSEMBLY | FLT | 511-1800-1-1 | THE HILLIARD CORP |  | 355B7029 | [13 empty] | .5 MICRON
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-008 |  | HYDRAULIC SUPPLY FILTER | FH2-2 | HYDRAULIC FILTER ASSEMBLY | FLT | 511-1800-1-1 | THE HILLIARD CORP |  | 355B7029 | [13 empty] | .5 MICRON
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-009 |  | MAIN HYDRAULIC PUMP | PH1-1 | ACCESSORY GEAR | PMP | PV3200R | DELAVAN MFG CO. |  | 355B7029 | [9 empty] | 1263 |  | 16.5 GPM | 1500 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-010 |  | AUXILIARY HYDRAULIC PUMP | PH2-1 | AUXILIARY SKID | PMP | PV3200R | DELAVAN MFG CO. |  | 355B7029 | [11 empty] | 16.5 GPM | 1500 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-011 |  | HYDRAULIC SYSTEM AIR BLEED VALVE - MAIN | VAB1-1 | HYDRAULIC MANIFOLD | VLV | AB04-15 | DENISON DIV., ABEX CORP |  | 355B7029
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-012 |  | HYDRAULIC SYSTEM AIR BLEED VALVE - AUX | VAB2-1 | HYDRAULIC MANIFOLD | VLV | AB04-15 | DENISON DIV., ABEX CORP |  | 355B7029
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-013 |  | HYDRAULIC PUMP CHECK VALVE - MAIN | VCK3-1 | HYDRAULIC MANIFOLD | VLV |  |  |  | 355B7029 | [11 empty] | 20 GPM | 5000 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-014 |  | HYDRAULIC PUMP CHECK VALVE - AUX | VCK3-2 | HYDRAULIC MANIFOLD | VLV |  |  |  | 355B7029 | [11 empty] | 20 GPM | 5000 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-015 |  | HYDRAULIC FILTER TRANSFER VALVE | VM4-1 | HYDRAULIC FILTER ASSEMBLY | VLV |  |  |  | 355B7029
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-016 |  | COMPENSATOR - HYDRAULIC SUPPLY PUMP - MAIN | VPR3-1 | MAIN HYDRAULIC PUMP | COMPN |  |  |  | 355B7029
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-017 |  | COMPENSATOR - HYDRAULIC SUPPLY PUMP - AUX | VPR3-2 | MAIN HYDRAULIC PUMP | COMPN |  |  |  | 355B7029
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-018 |  | MAIN HYDRAULIC PUMP RELIEF VALVE | VR21-1 | HYDRAULIC MANIFOLD | PRV |  |  |  | 355B7029 | [13 empty] | 1650 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-019 |  | AUX HYDRAULIC PUMP RELIEF VALVE | VR22-1 | HYDRAULIC MANIFOLD | PRV |  |  |  | 355B7029 | [13 empty] | 1650 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-020 |  | TURBINE OVERSPEED TRIP | 12HA-1 |  | TRP |  |  |  | 238B7057
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-021 |  | GAS FUEL STOP VALVE SOLENOID | 20FG-1 | TURBINE BASE | VLV | 4S-4640-2 | RUGGLES KLINGEMANN MFG CO. |  | 238B7057
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-022 |  | LIQUID FUEL STOP VALVE SOLENOID | 20FL-1 | TURBINE BASE | VLV | 4S-4640-2 | RUGGLES KLINGEMANN MFG CO. |  | 238B7057
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-023 |  | TURBINE COMPRESSOR IGV SOLENOID | 20TV-1 | TURBINE BASE | VLV | 4S-4640-2 | RUGGLES KLINGEMANN MFG CO. |  | 238B7057
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-024 |  | HYDRAULIC TRIP PRESSURE - GAS STOP VALVE | 63HG-1 | GAS STOP VALVE | PS |  |  |  | 238B7057 | [13 empty] | 20 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-025 |  | HYDRAULIC TRIP PRESSURE - GAS STOP VALVE | 63HG-2 | GAS STOP VALVE | PS |  |  |  | 238B7057 | [13 empty] | 20 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-026 |  | HYDRAULIC TRIP PRESSURE - GAS STOP VALVE | 63HG-3 | GAS STOP VALVE | PS |  |  |  | 238B7057 | [13 empty] | 20 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-027 |  | HYDRAULIC TRIP PRESSURE - LIQUID FUEL SYSTEM | 63HL-1 | TURBINE BASE | PS |  |  |  | 238B7057 | [13 empty] | 20 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-028 |  | HYDRAULIC TRIP PRESSURE - LIQUID FUEL SYSTEM | 63HL-2 | TURBINE BASE | PS |  |  |  | 238B7057 | [13 empty] | 20 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-029 |  | HYDRAULIC TRIP PRESSURE - LIQUID FUEL SYSTEM | 63HL-3 | TURBINE BASE | PS |  |  |  | 238B7057 | [13 empty] | 20 PSIG
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-030 |  | OVERSPEED BOLT TRIP ASSEMBLY | BOS-1 | ACCESSORY GEAR | BOS |  |  |  | 238B7057
GT HYDRAULIC SYSTEM | EX-09-1-X-01-08-031 |  | ELECTRO-HYDRAULIC SERVO VALVE | 65GC |  | VLV | 771 | MOOG INC
GT ENGINE | EX-09-1-X-01-01-001 |  | FLAME DETECTOR COMBUSTION CHAMBER 1 | 28FD-1 | GAS TURBINE | FD |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-002 |  | FLAME DETECTOR COMBUSTION CHAMBER 2 | 28FD-2A | GAS TURBINE | FD |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-003 |  | FLAME DETECTOR COMBUSTION CHAMBER 2 | 28FD-2B | GAS TURBINE | FD |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-004 |  | FLAME DETECTOR COMBUSTION CHAMBER 3 | 28FD-3 | GAS TURBINE | FD |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-005 |  | VIBRATION SENSOR | 39V-1A | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-006 |  | VIBRATION SENSOR | 39V-1B | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-007 |  | VIBRATION SENSOR | 39V-2A | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-008 |  | VIBRATION SENSOR | 39V-3A | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-009 |  | VIBRATION SENSOR | 39V-3B | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-010 |  | VIBRATION SENSOR | 39V-4A | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-011 |  | VIBRATION SENSOR | 39V-4B | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-012 |  | VIBRATION SENSOR | 39V-5A | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-013 |  | VIBRATION SENSOR - NON-CONTACT | 39VS-11 | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-014 |  | VIBRATION SENSOR - NON-CONTACT | 39VS-12 | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-015 |  | VIBRATION SENSOR - NON-CONTACT | 39VS-21 | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-016 |  | VIBRATION SENSOR - NON-CONTACT | 39VS-22 | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-017 |  | VIBRATION SENSOR - NON-CONTACT | 39VS-23 | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-018 |  | VIBRATION SENSOR - NON-CONTACT | 39VS-24 | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-019 |  | VIBRATION SENSOR - NON-CONTACT | 39VS-31 | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-020 |  | VIBRATION SENSOR - NON-CONTACT | 39VS-32 | GAS TURBINE | VIB |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-021 |  | SPEED PICKUP | 77NH-2 | GAS TURBINE | MPU |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-022 |  | SPEED PICKUP | 77NH-3 | GAS TURBINE | MPU |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-023 |  | KEYPHASOR BEARING #1 | 77RP-11 | GAS TURBINE | KP |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-024 |  | AXIAL POSITION TRANSMITTER | 96VC-11 | GAS TURBINE |  |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-025 |  | AXIAL POSITION TRANSMITTER | 96VC-12 | GAS TURBINE |  |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-026 |  | IGNITION EXCITER | 95SG-8 | GAS TURBINE | EXC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-027 |  | IGNITION EXCITER | 95SG-9 | GAS TURBINE | EXC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-028 |  | SPARK PLUG | 95SP-8 | GAS TURBINE | SP |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-029 |  | SPARK PLUG | 95SP-9 | GAS TURBINE | SP |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-030 |  | BEARING METAL TEMPERATURE SENSOR | BT-J1-1A | GAS TURBINE | TS |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-031 |  | BEARING METAL TEMPERATURE SENSOR | BT-J1-1B | GAS TURBINE | TS |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-032 |  | BEARING METAL TEMPERATURE SENSOR | BT-J1-2A | GAS TURBINE | TS |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-033 |  | BEARING METAL TEMPERATURE SENSOR | BT-J1-2B | GAS TURBINE | TS |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-034 |  | BEARING METAL TEMPERATURE SENSOR | BT-J2-1A | GAS TURBINE | TS |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-035 |  | BEARING METAL TEMPERATURE SENSOR | BT-J2-1B | GAS TURBINE | TS |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-036 |  | BEARING METAL TEMPERATURE SENSOR | BT-J2-2A | GAS TURBINE | TS |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-037 |  | BEARING METAL TEMPERATURE SENSOR | BT-J2-2B | GAS TURBINE | TS |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-038 |  | BEARING METAL TEMPERATURE SENSOR | BT-J3-1A | GAS TURBINE | TS |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-039 |  | BEARING METAL TEMPERATURE SENSOR | BT-J3-1B | GAS TURBINE | TS |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-040 |  | BEARING METAL TEMPERATURE SENSOR | BT-J3-2A | GAS TURBINE | TS |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-041 |  | BEARING METAL TEMPERATURE SENSOR | BT-J3-2B | GAS TURBINE | TS |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-042 |  | BEARING METAL THERMOCOUPLE | BT-TA1-1A | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-043 |  | BEARING METAL THERMOCOUPLE | BT-TA1-1B | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-044 |  | BEARING METAL THERMOCOUPLE | BT-TA1-2A | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-045 |  | BEARING METAL THERMOCOUPLE | BT-TA1-2B | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-046 |  | BEARING METAL THERMOCOUPLE | BT-TI1-1A | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-047 |  | BEARING METAL THERMOCOUPLE | BT-TI1-1B | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-048 |  | BEARING METAL THERMOCOUPLE | BT-TI1-2A | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-049 |  | BEARING METAL THERMOCOUPLE | BT-TI1-2B | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-050 |  | COMPRESSOR DISCHARGE THERMOCOUPLE | CT-DA-1 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-051 |  | COMPRESSOR DISCHARGE THERMOCOUPLE | CT-DA-2 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-052 |  | COMPRESSOR INLET THERMOCOUPLE | CT-IF-1 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-053 |  | COMPRESSOR INLET THERMOCOUPLE | CT-IF-2 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-054 |  | INNER BARREL TEMPERATURE SENSOR | TT-IB-1 | GAS TURBINE | TS |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-055 |  | WHEEL SPACE THERMOCOUPLE | TT-WS1AO-1 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-056 |  | WHEEL SPACE THERMOCOUPLE | TT-WS1AO-2 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-057 |  | WHEEL SPACE THERMOCOUPLE | TT-WS1FI-1 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-058 |  | WHEEL SPACE THERMOCOUPLE | TT-WS1FI-2 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-059 |  | WHEEL SPACE THERMOCOUPLE | TT-WS1FO-1 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-060 |  | WHEEL SPACE THERMOCOUPLE | TT-WS1FO-2 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-061 |  | WHEEL SPACE THERMOCOUPLE | TT-WS2AO-1 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-062 |  | WHEEL SPACE THERMOCOUPLE | TT-WS2AO-2 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-063 |  | WHEEL SPACE THERMOCOUPLE | TT-WS2FO-1 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-064 |  | WHEEL SPACE THERMOCOUPLE | TT-WS2FO-2 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-065 |  | WHEEL SPACE THERMOCOUPLE | TT-WS3AO-1 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-066 |  | WHEEL SPACE THERMOCOUPLE | TT-WS3AO-2 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-067 |  | WHEEL SPACE THERMOCOUPLE | TT-WSEFO-1 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-068 |  | WHEEL SPACE THERMOCOUPLE | TT-WSEFO-2 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-069 |  | EXHAUST THERMOCOUPLE | TT-XD-1 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-070 |  | EXHAUST THERMOCOUPLE | TT-XD-2 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-071 |  | EXHAUST THERMOCOUPLE | TT-XD-3 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-072 |  | EXHAUST THERMOCOUPLE | TT-XD-4 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-073 |  | EXHAUST THERMOCOUPLE | TT-XD-5 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-074 |  | EXHAUST THERMOCOUPLE | TT-XD-6 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-075 |  | EXHAUST THERMOCOUPLE | TT-XD-7 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-076 |  | EXHAUST THERMOCOUPLE | TT-XD-8 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-077 |  | EXHAUST THERMOCOUPLE | TT-XD-9 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-078 |  | EXHAUST THERMOCOUPLE | TT-XD-10 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-079 |  | EXHAUST THERMOCOUPLE | TT-XD-11 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-080 |  | EXHAUST THERMOCOUPLE | TT-XD-12 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-081 |  | EXHAUST THERMOCOUPLE | TT-XD-13 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-082 |  | EXHAUST THERMOCOUPLE | TT-XD-14 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-083 |  | EXHAUST THERMOCOUPLE | TT-XD-15 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-084 |  | EXHAUST THERMOCOUPLE | TT-XD-16 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-085 |  | EXHAUST THERMOCOUPLE | TT-XD-17 | GAS TURBINE | TC |  | GE |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-086 |  | EXHAUST THERMOCOUPLE | TT-XD-18 | GAS TURBINE | TC |  |  |  | 251B1645
GT ENGINE | EX-09-1-X-01-01-087 |  | VALVE, INLET GUIDE VANE SERVO | 90TV-1 | GAS TURBINE | VLV |  |  |  | 247B5397 | [11 empty] | 5 GPM | 1000 PSIG
GT ENGINE | EX-09-1-X-01-01-088 |  | LVDT, INLET GUIDE VANE | 96TV-1 | GAS TURBINE | LVDT |  |  |  | 247B5397
GT ENGINE | EX-09-1-X-01-01-089 |  | LVDT, INLET GUIDE VANE | 96TV-2 | GAS TURBINE | LVDT |  |  |  | 247B5397
GT ENGINE | EX-09-1-X-01-01-090 |  | FILTER, INLET GUIDE VANE SERVO | FH6-1 | GAS TURBINE | FLT |  |  |  | 247B5397 |  |  | 15 MICRON
GT ENGINE | EX-09-1-X-01-01-091 |  | VALVE, INLET FUIGE VANE DUMP | VH3-1 | GAS TURBINE | VLV |  |  |  | 247B5397
GT INTAKE | EX-09-1-X-01-03-001 |  | AIR INLET FILTER UNDERVOLTAGE - GENERATOR | 27GF-1 | GENERATOR INTAKE |  |  | GE |  | 251B1637
GT INTAKE | EX-09-1-X-01-03-002 |  | AIR INLET FILTER UNDERVOLTAGE - TURBINE | 27TF-1 | TURBINE INTAKE |  |  | GE |  | 251B1637
GT INTAKE | EX-09-1-X-01-03-003 |  | INLET AIR SELF CLEANING SEQUENCER - GENERATOR | 34GF-1 | GENERATOR INTAKE |  |  | GE |  | 251B1637 |  |  |  |  | 60 |  | 120 AC
GT INTAKE | EX-09-1-X-01-03-004 |  | INLET AIR SELF CLEANING SEQUENCER - TURBINE | 34TF-1 | TURBINE INTAKE |  |  | GE |  | 251B1637 |  |  |  |  | 60 |  | 120 AC
GT INTAKE | EX-09-1-X-01-03-005 |  | INLET AIR FILTER COMPRESSED AIR PRESSURE LOW | 63CA-1 | COMPRESSED AIR SUPPLY LINE | PS |  | GE |  | 251B1637 | [13 empty] | 60 PSIG
GT INTAKE | EX-09-1-X-01-03-006 |  | INLET AIR FILTER COMPRESSED AIR PRESSURE LOW | 63CA-3 | COMPRESSED AIR SUPPLY LINE | PS |  | GE |  | 251B1637 | [13 empty] | 60 PSIG
GT INTAKE | EX-09-1-X-01-03-007 |  | INLET AIR FILTER EXCESSIVE PRESSURE DROP - GENERATOR | 63GF-1 | GENERATOR INTAKE | PS |  | GE |  | 251B1637 | [13 empty] | 6" H2O
GT INTAKE | EX-09-1-X-01-03-008 |  | INLET AIR FILTER EXCESSIVE PRESSURE DROP - TURBINE ALARM | 63TF-1 | TURBINE INTAKE | PS |  | GE |  | 251B1637 | [13 empty] | 6" H2O
GT INTAKE | EX-09-1-X-01-03-009 |  | INLET AIR FILTER EXCESSIVE PRESSURE DROP - TURBINE TRIP | 63TF-2A | TURBINE INTAKE | PS |  | GE |  | 251B1637 | [13 empty] | 8" H2O
GT INTAKE | EX-09-1-X-01-03-010 |  | INLET AIR FILTER EXCESSIVE PRESSURE DROP - TURBINE TRIP | 63TF-2B | TURBINE INTAKE | PS |  | GE |  | 251B1637 | [13 empty] | 8" H2O
GT INTAKE | EX-09-1-X-01-03-011 |  | RELATIVE HUMIDITY DETECTOR | 95RH-1 | TURBINE INTAKE |  |  | GE |  | 251B1637
GT INTAKE | EX-09-1-X-01-03-012 |  | FILTER, INLET AIR |  | TURBINE INTAKE | FLT | OSM-38333-1 | DONALDSON |  | 251B1637
GT EXHAUST | EX-09-1-X-01-04-001 |  | EXHAUST DUCT PRESSURE HIGH ALARM | 63EA-1 | TURBINE EXHAUST DUCT | PS |  | GE |  | 251B1637 | [13 empty] | 16" H2O
GT EXHAUST | EX-09-1-X-01-04-002 |  | EXHAUST DUCT PRESSURE HIGH NORMAL SHUTDOWN | 63ET-1 | TURBINE EXHAUST DUCT | PS |  | GE |  | 251B1637 | [13 empty] | 20" H20
GT EXHAUST | EX-09-1-X-01-04-003 |  | EXHAUST DUCT PRESSURE HIGH TRIP | 63ET-2 | TURBINE EXHAUST DUCT | PS |  | GE |  | 251B1637 | [13 empty] | 20" H20
GT EXHAUST | EX-09-1-X-01-04-004 |  | BLOWER ASSY, EXHAUST FRAME |  | TURBINE COMPARTMENT, TOP | BLWR | 404CB | MOTOR - RELIANCE, FAN - ILLINOIS BLOWER | [6 empty] | 60 | 3 | 480 |  |  | 3600 | 60 | 2240/3800 CFM
GT FIRE PROTECTION | EX-09-1-X-01-09-001 |  | FIRE PROTECTION CO2 TIMER - ZONE 1, INITIAL | 2CP-1A | CO2 ELECTRICAL CONTROL PANEL | TMR |  |  |  | 251B1656
GT FIRE PROTECTION | EX-09-1-X-01-09-002 |  | FIRE PROTECTION CO2 TIMER - ZONE 1, EXTENDED | 2CP-2A | CO2 ELECTRICAL CONTROL PANEL | TMR |  |  |  | 251B1656
GT FIRE PROTECTION | EX-09-1-X-01-09-003 |  | FIRE PROTECTION CO2 TIMER - ZONE 2, INITIAL | 2CP-3A | CO2 ELECTRICAL CONTROL PANEL | TMR |  |  |  | 251B1656
GT FIRE PROTECTION | EX-09-1-X-01-09-004 |  | FIRE PROTECTION CO2 TIMER - ZONE 2, EXTENDED | 2CP-4A | CO2 ELECTRICAL CONTROL PANEL | TMR |  |  |  | 251B1656
GT FIRE PROTECTION | EX-09-1-X-01-09-005 |  | CO2 RELEASE BLOCKING DEVICE | 33CL-1A
GT FIRE PROTECTION | EX-09-1-X-01-09-006 |  | FIRE PROTECTION CO2 RELEASE SWITCH - ZONE 1 | 43CP-1A | CO2 ELECTRICAL CONTROL PANEL | SW |  |  |  | 251B1656
GT FIRE PROTECTION | EX-09-1-X-01-09-007 |  | FIRE PROTECTION CO2 RELEASE SWITCH - ZONE 2 | 43CP-2A | CO2 ELECTRICAL CONTROL PANEL | SW |  |  |  | 251B1656
GT FIRE PROTECTION | EX-09-1-X-01-09-008 |  | FIRE PROTECTION CO2 TIMER RESET | 86FP-1A | CO2 ELECTRICAL CONTROL PANEL | PB |  |  |  | 251B1656
GT FIRE PROTECTION | EX-09-1-X-01-09-009 |  | FIRE PROTECTION CO2 TIMER RESET | 86FP-2A | CO2 ELECTRICAL CONTROL PANEL | PB |  |  |  | 251B1656
GT FIRE PROTECTION | EX-09-1-X-01-09-010 |  | CO2 SYSTEM BLEED VALVE | VR7-1 | CO2 SKID | VLV |  |  |  | 251B1656 | [13 empty] | 341 PSIG
GT FIRE PROTECTION | EX-09-1-X-01-09-011 |  | CO2 SYSTEM RELIEF VALVE | VR8-1 | CO2 SKID | VLV |  |  |  | 251B1656 | [13 empty] | 357 PSIG
GT FIRE PROTECTION | EX-09-1-X-01-09-012 |  | CO2 SYSTEM RELIEF VALVE | VR9-1 | CO2 SKID | VLV |  |  |  | 251B1656 | [13 empty] | 357 PSIG
GT FIRE PROTECTION | EX-09-1-X-01-09-013 |  | CO2 REFRIGERATION COMPRESSOR MOTOR | 88RC-1 | CO2 SKID | MOT |  | CHEMETRON FIRE SYSTEMS |  | 251B1656 |  |  |  |  | 60 | 1 | 220 AC |  |  | 1800 | 0.75
GT FIRE PROTECTION | EX-09-1-X-01-09-014 |  | FIRE ALARM BELL | LS2-1 | OFF BASE ENCLOSURE | BELL |  |  |  | 251B1656
GT FIRE PROTECTION | EX-09-1-X-01-09-015 |  | FIRE PROTECTION CO2 PRESSURE SWITCH - ZONE 1 | 45CP-1A | PILOT CONTROL CABINET | PS |  |  |  | 251B1656
GT FIRE PROTECTION | EX-09-1-X-01-09-016 |  | FIRE PROTECTION CO2 PRESSURE SWITCH - ZONE 2 | 45CP-2A | PILOT CONTROL CABINET | PS |  |  |  | 251B1656
GT FIRE PROTECTION | EX-09-1-X-01-09-017 |  | FIRE PROTECTION CO2 RELEASE SOLENOID VALVE - ZONE 1 | 45CR-1A | PILOT CONTROL CABINET | VLV |  |  |  | 251B1656
GT FIRE PROTECTION | EX-09-1-X-01-09-018 |  | FIRE PROTECTION CO2 RELEASE SOLENOID VALVE - ZONE 1 | 45CR-2A | PILOT CONTROL CABINET | VLV |  |  |  | 251B1656
GT FIRE PROTECTION | EX-09-1-X-01-09-019 |  | FIRE PROTECTION CO2 RELEASE SOLENOID VALVE - ZONE2 | 45CR-3A | PILOT CONTROL CABINET | VLV |  |  |  | 251B1656
GT FIRE PROTECTION | EX-09-1-X-01-09-020 |  | FIRE PROTECTION CO2 RELEASE SOLENOID VALVE - ZONE2 | 45CR-4A | PILOT CONTROL CABINET | VLV |  |  |  | 251B1656
GT FIRE PROTECTION | EX-09-1-X-01-09-021 |  | FIRE DETECTOR - ACCESSORY COMPARTMENT | 45FA-1A | ACCESSORY COMPARTMENT | FT |  |  |  | 251B1656 | [13 empty] | 600 DEG. F
GT FIRE PROTECTION | EX-09-1-X-01-09-022 |  | FIRE DETECTOR - ACCESSORY COMPARTMENT | 45FA-1B | ACCESSORY COMPARTMENT | FT |  |  |  | 251B1656 | [13 empty] | 600 DEG. F
GT FIRE PROTECTION | EX-09-1-X-01-09-023 |  | FIRE DETECTOR - ACCESSORY COMPARTMENT | 45FA-2A | ACCESSORY COMPARTMENT | FT |  |  |  | 251B1656 | [13 empty] | 600 DEG. F
GT FIRE PROTECTION | EX-09-1-X-01-09-024 |  | FIRE DETECTOR - ACCESSORY COMPARTMENT | 45FA-2B | ACCESSORY COMPARTMENT | FT |  |  |  | 251B1656 | [13 empty] | 600 DEG. F
GT FIRE PROTECTION | EX-09-1-X-01-09-025 |  | FIRE DETECTOR - TURBINE COMPARTMENT | 45FT-1A | TURBINE COMPARTMENT | FT |  |  |  | 251B1656 | [13 empty] | 600 DEG. F
GT FIRE PROTECTION | EX-09-1-X-01-09-026 |  | FIRE DETECTOR - TURBINE COMPARTMENT | 45FT-1B | TURBINE COMPARTMENT | FT |  |  |  | 251B1656 | [13 empty] | 600 DEG. F
GT FIRE PROTECTION | EX-09-1-X-01-09-027 |  | FIRE DETECTOR - TURBINE COMPARTMENT | 45FT-2A | TURBINE COMPARTMENT | FT |  |  |  | 251B1656 | [13 empty] | 600 DEG. F
GT FIRE PROTECTION | EX-09-1-X-01-09-028 |  | FIRE DETECTOR - TURBINE COMPARTMENT | 45FT-2B | TURBINE COMPARTMENT | FT |  |  |  | 251B1656 | [13 empty] | 600 DEG. F
GT FIRE PROTECTION | EX-09-1-X-01-09-029 |  | FIRE DETECTOR - TURBINE COMPARTMENT | 45FT-3A | TURBINE COMPARTMENT | FT |  |  |  | 251B1656 | [13 empty] | 600 DEG. F
GT FIRE PROTECTION | EX-09-1-X-01-09-030 |  | FIRE DETECTOR - TURBINE COMPARTMENT | 45FT-3B | TURBINE COMPARTMENT | FT |  |  |  | 251B1656 | [13 empty] | 600 DEG. F
GT FIRE PROTECTION | EX-09-1-X-01-09-031 |  | FIRE DETECTOR - TURBINE COMPARTMENT | 45FT-8A | EXHAUST | FT |  |  |  | 251B1656 | [13 empty] | 950 DEG. F
GT FIRE PROTECTION | EX-09-1-X-01-09-032 |  | FIRE DETECTOR - TURBINE COMPARTMENT | 45FT-8B | EXHAUST | FT |  |  |  | 251B1656 | [13 empty] | 950 DEG. F
GT FIRE PROTECTION | EX-09-1-X-01-09-033 |  | FIRE DETECTOR - TURBINE COMPARTMENT | 45FT-9A | LOAD SHAFT COMPARTMENT | FT |  |  |  | 251B1656 | [13 empty] | 600 DEG. F
GT FIRE PROTECTION | EX-09-1-X-01-09-034 |  | FIRE DETECTOR - TURBINE COMPARTMENT | 45FT-9B | LOAD SHAFT COMPARTMENT | FT |  |  |  | 251B1656 | [13 empty] | 600 DEG. F
GT FIRE PROTECTION | EX-09-1-X-01-09-035 |  | CO2 STORAGE TANK |  | CO2 SKID | TNK |  | CHEMETRON FIRE SYSTEMS |  | 251B1656 |  | STEEL | 4 TONS
GT FUEL OIL | EX-09-1-X-01-06-001 |  | SOLENOID - FUEL CLUTCH | 20CF-1 | MAIN FUEL PUMP ASSY | SOL | 9000 | THE CARLYLE JOHNSON MACHINE CO. |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-002 |  | LIMIT SWITCH - LIQUID FUEL STOP VALVE | 33FL-1 | LIQUID FUEL STOP VALVE | LS |  |  |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-003 |  | LIMIT SWITCH - LIQUID FUEL STOP VALVE | 33FL-2 | LIQUID FUEL STOP VALVE | LS |  |  |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-004 |  | SERVO VALVE - LIQUID FUEL PUMP BYPASS | 65FP-1 |  | VLV |  |  |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-005 |  | PICKUP, SPEED - FLOW DIVIDER MAG | 77FD-1 | GAS TURBINE | SPU |  |  |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-006 |  | PICKUP, SPEED - FLOW DIVIDER MAG | 77FD-2 | GAS TURBINE | SPU |  |  |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-007 |  | PICKUP, SPEED - FLOW DIVIDER MAG | 77FD-3 | GAS TURBINE | SPU |  |  |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-008 |  | LVDT - LIQUID FUEL PUMP BYPASS VALVE | 96FP-1 | FUEL PUMP BYPASS VALVE | LVDT |  |  |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-009 |  | LVDT - LIQUID FUEL PUMP BYPASS VALVE | 96FP-2 | FUEL PUMP BYPASS VALVE | LVDT |  |  |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-010 |  | FLOW DIVIDER | FD1-1 | GAS TURBINE | FD |  | ROPER PUMP CO. |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-011 |  | FILTER - SECONDARY HIGH PRESSURE | FF2-1 | FUEL SUPPLY LINE | FLT | HP-718-1440-3XESS | THE HILLIARD CORP |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-012 |  | FILTER - HYD SUPPLY FILTER, LIQUID FUEL SERVO | FH3-1 | HYDRAULIC SUPPLY LINE TO SERVO | FLT |  |  |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-013 |  | PUMP - MAIN FUEL | PF1-1 | ACCESSORY GEAR BOX | PMP | B2216A | WARREN CO. |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-014 |  | VALVE - FALSE START DRAIN | VA17-1 | COMBUSTOR WRAPPER | VLV | CYS516J42LCS | RG LAURENCE CO. |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-015 |  | VALVE - FALSE START DRAIN | VA17-2 | EXHAUST FRAME | VLV |  |  |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-016 |  | VALVE - DRAIN | VA17-5 | EXHAUST PLENUM | VLV |  |  |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-017 |  | VALVE, CHECK - LIQUID FUEL NOZZLE | VCK1-1 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 120 + - 12 PSIG
GT FUEL OIL | EX-09-1-X-01-06-018 |  | VALVE, CHECK - LIQUID FUEL NOZZLE | VCK1-2 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 121 + - 12 PSIG
GT FUEL OIL | EX-09-1-X-01-06-019 |  | VALVE, CHECK - LIQUID FUEL NOZZLE | VCK1-3 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 122 + - 12 PSIG
GT FUEL OIL | EX-09-1-X-01-06-020 |  | VALVE, CHECK - LIQUID FUEL NOZZLE | VCK1-4 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 123 + - 12 PSIG
GT FUEL OIL | EX-09-1-X-01-06-021 |  | VALVE, CHECK - LIQUID FUEL NOZZLE | VCK1-5 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 124 + - 12 PSIG
GT FUEL OIL | EX-09-1-X-01-06-022 |  | VALVE, CHECK - LIQUID FUEL NOZZLE | VCK1-6 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 125 + - 12 PSIG
GT FUEL OIL | EX-09-1-X-01-06-023 |  | VALVE, CHECK - LIQUID FUEL NOZZLE | VCK1-7 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 126 + - 12 PSIG
GT FUEL OIL | EX-09-1-X-01-06-024 |  | VALVE, CHECK - LIQUID FUEL NOZZLE | VCK1-8 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 127 + - 12 PSIG
GT FUEL OIL | EX-09-1-X-01-06-025 |  | VALVE, CHECK - LIQUID FUEL NOZZLE | VCK1-9 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 128 + - 12 PSIG
GT FUEL OIL | EX-09-1-X-01-06-026 |  | VALVE, CHECK - LIQUID FUEL NOZZLE | VCK1-10 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 129 + - 12 PSIG
GT FUEL OIL | EX-09-1-X-01-06-027 |  | VALVE, CHECK - LIQUID FUEL NOZZLE PURGE | VCK2-1 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 3 PSIG
GT FUEL OIL | EX-09-1-X-01-06-028 |  | VALVE, CHECK - LIQUID FUEL NOZZLE PURGE | VCK2-2 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 3 PSIG
GT FUEL OIL | EX-09-1-X-01-06-029 |  | VALVE, CHECK - LIQUID FUEL NOZZLE PURGE | VCK2-3 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 3 PSIG
GT FUEL OIL | EX-09-1-X-01-06-030 |  | VALVE, CHECK - LIQUID FUEL NOZZLE PURGE | VCK2-4 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 3 PSIG
GT FUEL OIL | EX-09-1-X-01-06-031 |  | VALVE, CHECK - LIQUID FUEL NOZZLE PURGE | VCK2-5 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 3 PSIG
GT FUEL OIL | EX-09-1-X-01-06-032 |  | VALVE, CHECK - LIQUID FUEL NOZZLE PURGE | VCK2-6 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 3 PSIG
GT FUEL OIL | EX-09-1-X-01-06-033 |  | VALVE, CHECK - LIQUID FUEL NOZZLE PURGE | VCK2-7 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 3 PSIG
GT FUEL OIL | EX-09-1-X-01-06-034 |  | VALVE, CHECK - LIQUID FUEL NOZZLE PURGE | VCK2-8 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 3 PSIG
GT FUEL OIL | EX-09-1-X-01-06-035 |  | VALVE, CHECK - LIQUID FUEL NOZZLE PURGE | VCK2-9 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 3 PSIG
GT FUEL OIL | EX-09-1-X-01-06-036 |  | VALVE, CHECK - LIQUID FUEL NOZZLE PURGE | VCK2-10 | GAS TURBINE | VLV |  |  |  | 251B1651 | [13 empty] | 3 PSIG
GT FUEL OIL | EX-09-1-X-01-06-037 |  | VALVE - LIQUID FUEL STOP VALVE HYD TRIP | VH4-1 | TURBINE BASE | VLV |  |  |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-038 |  | VALVE, RELIEF - MAIN FUEL PUMP PRESSURE | VR4-1 | MAIN FUEL PUMP ASSY | VLV | 1900/70/75/80/82 | CONSOLIDATED IND VALVE |  | 251B1651
GT FUEL OIL | EX-09-1-X-01-06-039 |  | VALVE - FUEL OIL STOP | VS1-1 | LIQUID FUEL SUPPLY LINE | VLV |  |  |  | 251B1651
GT FUEL GAS | EX-09-1-X-01-07-001 |  | SOLENOID VALVE, FUEL GAS VENT | 20VG-1 |  | VLV |  | ASCO |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-002 |  | SOLENOID VALVE, FUEL GAS PURGE | 20PG-1 |  | VLV |  | ASCO |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-003 |  | SOLENOID VALVE, FUEL GAS PURGE | 20PG-2 |  | VLV |  | ASCO |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-004 |  | SOLENOID VALVE, FUEL GAS VENT | 20VG-2 |  | VLV |  | ASCO |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-005 |  | SWITCH, PRESSURE - GAS FUEL PRESSURE | 63FG-3 |  | PS |  |  |  | 251B1387 | [13 empty] | 285 PSIG
GT FUEL GAS | EX-09-1-X-01-07-006 |  | SERVO VALVE, GAS CONTROL | 65GC-1 |  | VLV | 771 | MOOG |  | 251B1387 | [11 empty] | 5 GPM | 1000 PSID
GT FUEL GAS | EX-09-1-X-01-07-007 |  | SERVO, STOP/RATIO | 90SR-1 |  | SRVO | 771 | MOOG |  | 251B1387 | [11 empty] | 5 GPM | 1000 PSID
GT FUEL GAS | EX-09-1-X-01-07-008 |  | PRESSURE TRANSMITTER, FUEL GAS FLOW ORIFICE | 96FF-1 | TRANSDUCER MANIFOLD | PT | 1151DP | ROSEMOUNT |  | 251B1387 | [13 empty] | 0 - 30 IN. WATER
GT FUEL GAS | EX-09-1-X-01-07-009 |  | PRESSURE TRANSMITTER, FUEL GAS FLOW ORIFICE | 96FF-2 | TRANSDUCER MANIFOLD | PT | 1151DP | ROSEMOUNT |  | 251B1387 | [13 empty] | 0 - 30 IN. WATER
GT FUEL GAS | EX-09-1-X-01-07-010 |  | PRESSURE TRANSMITTER, NOX REDUCTION | 96FG-1 | TRANSDUCER MANIFOLD | PT |  |  |  | 251B1387 | [13 empty] | 0 - 400 PSIG
GT FUEL GAS | EX-09-1-X-01-07-011 |  | PRESSURE TRANSMITTER, INTERSTAGE FUEL PRESSURE | 96FG-2A | TURBINE BASE | PT |  |  |  | 251B1387 | [13 empty] | 0 - 300 PSIG
GT FUEL GAS | EX-09-1-X-01-07-012 |  | PRESSURE TRANSMITTER, INTERSTAGE FUEL PRESSURE | 96FG2B | TURBINE BASE | PT |  |  |  | 251B1387 | [13 empty] | 0 - 300 PSIG
GT FUEL GAS | EX-09-1-X-01-07-013 |  | PRESSURE TRANSMITTER, INTERSTAGE FUEL PRESSURE | 96FG-2C | TURBINE BASE | PT |  |  |  | 251B1387 | [13 empty] | 0 - 300 PSIG
GT FUEL GAS | EX-09-1-X-01-07-014 |  | LVDT, GAS CONTROL VALVE | 96GC-1 | GAS CONTROL VALVE | LVDT |  |  |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-015 |  | LVDT, GAS CONTROL VALVE | 96GC-2 | GAS CONTROL VALVE | LVDT |  |  |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-016 |  | LVDT, STOP/RATIO VALVE | 96SR-1 | STOP/RATIO VALVE | LVDT |  |  |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-017 |  | LVDT, STOP/RATIO VALVE | 96SR-2 | STOP/RATIO VALVE | LVDT |  |  |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-018 |  | FILTER, FUEL SERVO HYD SUPPLY | FH7-1 | HYDRAULIC SUPPLY LINE | FLT |  |  |  | 251B1387 |  |  | 15 MICRON
GT FUEL GAS | EX-09-1-X-01-07-019 |  | THERMOCOUPLE, FUEL GAS TEMP | FT-GI-1 | GAS SUPPLY LINE | TC | TYPE K |  |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-020 |  | THERMOCOUPLE, FUEL GAS TEMP | FT-GI-2 | GAS SUPPLY LINE | TC | TYPE K |  |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-021 |  | THERMOCOUPLE, FUEL GAS TEMP | FT-GI-3 | GAS SUPPLY LINE | TC | TYPE K |  |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-022 |  | NOZZLE, GAS FUEL | MG1-1 | COMBUSTOR | NOZ |  |  |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-023 |  | ORIFICE, GAS FUEL METER TUBE | MG2-1 |  | ORF |  |  |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-024 |  | ASSEMBLY, GAS VALVE | VGA-1 | FUEL GAS SKID | VLV |  |  |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-025 |  | VALVE, GAS CONTROL | VGC-1 | FUEL GAS SKID | VLV |  |  |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-026 |  | VALVE, STOP/RATIO DUMP | VH5-1 | STOP/RATIO VALVE | VLV |  |  |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-027 |  | VALVE, STOP/RATIO | VSR-1 |  | VLV |  |  |  | 251B1387
GT FUEL GAS | EX-09-1-X-01-07-028 |  | VALVE, AIR TO PURGE | VPR54-1 |  | VLV | 67FR108 | FISHER | [15 empty] | 47.5 PSIG
GT HVAC | EX-09-1-X-01-10-001 |  | SWITCH, TEMP - TURBINE COMPARTMENT | 26BT-1 | TURBINE COMPARTMENT | TS |  |  |  | 251B1654 | [13 empty] | 300 DEG F
GT HVAC | EX-09-1-X-01-10-002 |  | SWITCH, TEMP - TURBINE COMPARTMENT | 26BT-2 | TURBINE COMPARTMENT | TS |  |  |  | 251B1654 | [13 empty] | 115 DEG F
GT HVAC | EX-09-1-X-01-10-003 |  | THERMOSTAT, LOAD COUPLING COMPARTMENT | 26VG-2 | LOAD COMPARTMENT | THERMO |  |  |  | 251B1654 | [13 empty] | 117 DEG F
GT HVAC | EX-09-1-X-01-10-004 |  | MOTOR, COOLING AIR FAN | 88BA-1 | ACCESS COMPARTMENT | MOT |  | R.K. CHASE |  | 251B1654 |  |  |  |  | 60 | 3 | 460 |  |  | 1200 | 3
GT HVAC | EX-09-1-X-01-10-005 |  | MOTOR, COOLING AIR FAN | 88BT-1 | TURBINE COMPARTMENT | MOT |  | R.K. CHASE |  | 251B1654 |  |  |  |  | 60 | 3 | 460 |  |  | 1150 | 15
GT HVAC | EX-09-1-X-01-10-006 |  | AIR CONDITIONER | 88KA-1 | POWER CONTROL COMPARTMENT | AC | SL24D30 | FRIEDRICH AIR CONDITIONING |  | 251B1654 |  |  |  |  | 60 | 1 | 230
GT HVAC | EX-09-1-X-01-10-007 |  | AIR CONDITIONER | 88KA-2 | POWER CONTROL COMPARTMENT | AC | SL24D30 | FRIEDRICH AIR CONDITIONING |  | 251B1654 |  |  |  |  | 60 | 1 | 230
GT HVAC | EX-09-1-X-01-10-008 |  | MOTOR, COOLING AIR FAN | 88VG-1 | LOAD COMPARTMENT | MOT |  | R.K. CHASE |  | 251B1654 |  |  |  |  | 60 | 3 | 460 |  |  | 3500 | 5
GT STARTING SYSTEM | EX-09-1-X-01-11-001 |  | SOLENOID VALVE, TORQUE CONVERTER FILL/DRAIN | 20TU-1 | STARTER | VLV | EL7-5ZFT | VOITH GETRIEBE KG HEIDENHEIM |  | 355B7030
GT STARTING SYSTEM | EX-09-1-X-01-11-002 |  | SOLENOID VALVE, TORQUE CONVERTER FILL/DRAIN | 20TU-2 | STARTER | VLV | EL7-5ZFT | VOITH GETRIEBE KG HEIDENHEIM |  | 355B7030
GT STARTING SYSTEM | EX-09-1-X-01-11-003 |  | HEATER, SPACE - CRANKING MOTOR | 23CR-1 | CRANKING MOTOR | HTR |  |  |  | 355B7030 |  |  |  |  | 60 | 1 | 120 |  | 800
GT STARTING SYSTEM | EX-09-1-X-01-11-004 |  | SWITCH, TORQUE ADJUSTER TORQUE, MIN TRAVEL | 33TM-1 | TORQUE CONVERTER | SW |  |  |  | 355B7030
GT STARTING SYSTEM | EX-09-1-X-01-11-005 |  | SWITCH, TORQUE ADJUSTER TORQUE, MAX TRAVEL | 33TM-2 | TORQUE CONVERTER | SW |  |  |  | 355B7030
GT STARTING SYSTEM | EX-09-1-X-01-11-006 |  | SWITCH, LIMIT - TORQUE ADJUSTER MIN TRAVEL | 33TM-3 | TORQUE CONVERTER | LS |  |  |  | 355B7030
GT STARTING SYSTEM | EX-09-1-X-01-11-007 |  | SWITCH, LIMIT - TORQUE ADJUSTER MAX TRAVEL | 33TM-4 | TORQUE CONVERTER | LS |  |  |  | 355B7030
GT STARTING SYSTEM | EX-09-1-X-01-11-008 |  | SWITCH, LIMIT - TORQUE ADJUSTER ACCEL TORQUE | 33TM-5 | TORQUE CONVERTER | LS |  |  |  | 355B7030
GT STARTING SYSTEM | EX-09-1-X-01-11-009 |  | SWITCH, LIMIT - TORQUE ADJUSTER FIRING TORQUE | 33TM-6 | TORQUE CONVERTER | LS |  |  |  | 355B7030
GT STARTING SYSTEM | EX-09-1-X-01-11-010 |  | MOTOR, STARTING | 88CR-1 | ACCESSORY GEARBOX | MOT |  | GE |  | 355B7030 |  |  |  |  | 60 | 3 | 4160 |  |  | 3600 | 800
GT STARTING SYSTEM | EX-09-1-X-01-11-011 |  | MOTOR, TORQUE/SPEED ADJUSTER | 88TM-1 | ACCESSORY GEARBOX | MOT | EL7-5Z GTM | VOITH GETRIEBE KG HEIDENHEIM |  | 355B7030 |  |  |  |  | 60 | 3 | 460 |  |  | 1800 | 1
GT STARTING SYSTEM | EX-09-1-X-01-11-012 |  | RTD, STARTING MOTOR STATOR TEMP | ET-CRS-1/R | STARTING MOTOR | RTD |  |  |  | 355B7030 | [13 empty] | 100 OHM
GT STARTING SYSTEM | EX-09-1-X-01-11-013 |  | RTD, STARTING MOTOR STATOR TEMP | ET-CRS-2/R | STARTING MOTOR | RTD |  |  |  | 355B7030 | [13 empty] | 100 OHM
GT STARTING SYSTEM | EX-09-1-X-01-11-014 |  | RTD, STARTING MOTOR STATOR TEMP | ET-CRS-3/R | STARTING MOTOR | RTD |  |  |  | 355B7030 | [13 empty] | 100 OHM
GT STARTING SYSTEM | EX-09-1-X-01-11-015 |  | RTD, STARTING MOTOR STATOR TEMP | ET-CRS-4/R | STARTING MOTOR | RTD |  |  |  | 355B7030 | [13 empty] | 10 OHM
GT STARTING SYSTEM | EX-09-1-X-01-11-016 |  | RTD, STARTING MOTOR STATOR TEMP | ET-CRS-5/R | STARTING MOTOR | RTD |  |  |  | 355B7030 | [13 empty] | 10 OHM
GT STARTING SYSTEM | EX-09-1-X-01-11-017 |  | RTD, STARTING MOTOR STATOR TEMP | ET-CRS-6/R | STARTING MOTOR | RTD |  |  |  | 355B7030 | [13 empty] | 10 OHM
GT WATER INJECTION | EX-09-1-X-01-13-001 |  | SOLENOID VALVE, WATER INJECTION STOP | 20WN-4 |  | VLV |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-002 |  | SOLENOID VALVE, WATER INJECTION STAGING | 20WN-5 |  | VLV |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-003 |  | HEATER, WATER INJECTION MOTOR | 23WN-1 | WATER INJECTION PUMP MOTOR | HTR |  |  |  | 251B1268 |  |  |  |  | 60 | 1 | 120 |  | 100
GT WATER INJECTION | EX-09-1-X-01-13-004 |  | HEATER, WATER INJECTION SKID | 23WR-1 | WATER INJ SKID COMPARTMENT | HTR |  |  |  | 251B1268 |  |  |  |  | 60 | 3 | 480 |  | 25
GT WATER INJECTION | EX-09-1-X-01-13-005 |  | SWITCH, WATER INJECTION TEMP | 26JS-1 | WATER INJECTION PIPING | TS |  |  |  | 251B1268 | [13 empty] | 90 DEG F
GT WATER INJECTION | EX-09-1-X-01-13-006 |  | SWITCH, WATER INJECTION TEMP | 26JS-2 | WATER INJECTION PIPING | TS |  |  |  | 251B1268 | [13 empty] | 140 DEG F
GT WATER INJECTION | EX-09-1-X-01-13-007 |  | THERMOSTAT, WATER INJECTION SKID | 26WR-1 | WATER INJ SKID COMPARTMENT | THERMO |  |  |  | 251B1268 | [13 empty] | 50 DEG F
GT WATER INJECTION | EX-09-1-X-01-13-008 |  | SWITCH, WATER INJECTION SKID AMBIENT TEMP LOW | 26WR-2 | WATER INJ SKID COMPARTMENT | TS |  |  |  | 251B1268 | [13 empty] | 40 DEG F
GT WATER INJECTION | EX-09-1-X-01-13-009 |  | SWITCH, LIMIT - WATER INJECTION STOP VALVE | 33WN-1 | WATER INJECTION STOP VALVE | LS |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-010 |  | SWITCH, LIMIT - WATER INJECTION ISOLATION VALVE | 33WN-2 | WATER INJECTION ISOLATION VALVE | LS |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-011 |  | SWITCH, PRESSURE, WATER INJ HYD TRIP | 63HW-1 |  | PS |  |  |  | 251B1268 | [13 empty] | 20 PSIG
GT WATER INJECTION | EX-09-1-X-01-13-012 |  | SWITCH, PRESSURE, WATER INJECTION | 63WN-1 |  | PS |  |  |  | 251B1268 | [13 empty] | 8 IN. WATER
GT WATER INJECTION | EX-09-1-X-01-13-013 |  | SWITCH, PRESSURE, WATER INJECTION | 63WN-2 |  | PS |  |  |  | 251B1268 | [13 empty] | 480 PSIG
GT WATER INJECTION | EX-09-1-X-01-13-014 |  | SWITCH, DIFF PRESSURE, WATER INJECTION | 63WN-3 |  | PS |  |  |  | 251B1268 | [13 empty] | 20 PSID
GT WATER INJECTION | EX-09-1-X-01-13-015 |  | SWITCH, FLOW - WATER INJECTION | 77WN-1 |  | FS |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-016 |  | SWITCH, FLOW - WATER INJECTION | 77WN-2 |  | FS |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-017 |  | SWITCH, FLOW - WATER INJECTION | 77WN-3 |  | FS |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-018 |  | SWITCH, FLOW - WATER INJECTION | 77WN-4 |  | FS |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-019 |  | MOTOR, WATER INJ SKID COOLING FAN | 88JS-1 | WATER INJECTION SKID | MOT |  |  |  | 251B1268 |  |  |  |  | 60 | 1 | 120 |  |  | 1725 | 0.5
GT WATER INJECTION | EX-09-1-X-01-13-020 |  | MOTOR/PUMP ASSY, WATER INJECTION | 88WN-1 | WATER INJECTION SKID | MOT | ROA-111 | MOTOR - GE, PUMP - ENVIROTECH |  | 251B1268 |  |  | S-600 | 405TS | 60 | 3 | 460 |  |  | 3600 | 125 | 140 GPM
GT WATER INJECTION | EX-09-1-X-01-13-021 |  | ACTUATOR, WATER INJ FLOW CONTROL VALVE | 90WN-1 | FLOW CONTROL VALVE | ACT |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-022 |  | FLOW TRANSMITTER, WATER INJ FLOW CONTOL VALVE POSITION | 96WN-1 |  | FT |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-023 |  | LIGHT, AC - WATER INJECTION SKID | AL-58 | WATER INJECTION SKID | LIGHT |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-024 |  | LIGHT, AC - WATER INJECTION SKID | AL-59 | WATER INJECTION SKID | LIGHT |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-025 |  | RECEPTACLE, WATER INJECTION SKID | AR-41 | WATER INJECTION SKID | RECPT |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-026 |  | RECEPTACLE, WATER INJECTION SKID | AR-42 | WATER INJECTION SKID | RECPT |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-027 |  | SWITCH, AC LIGHTING - WATER INJECTION SKDI | ASW-28 | WATER INJECTION SKID | LIGHT SW |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-028 |  | LIGHT, DC - WATER INJECTION SKID | DL-18 | WATER INJECTION SKID | LIGHT |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-029 |  | LIGHT, DC - WATER INJECTION SKID | DL-20 | WATER INJECTION SKID | LIGHT |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-030 |  | FILTER, HYD. - WATER INJECTION STOP VALVE | FH11-1 | WATER INJECTION STOP VALVE | FLT |  |  |  | 251B1268 |  |  | 15 MICRON
GT WATER INJECTION | EX-09-1-X-01-13-031 |  | FILTER, HYD. - WATER INJECTION STAGING VALVE | FH12-1 | WATER INJECTION STAGING VALVE | FLT |  |  |  | 251B1268 |  |  | 15 MICRON
GT WATER INJECTION | EX-09-1-X-01-13-032 |  | METER, FLOW - WATER INJECTION | FM1-1 | WATER INJECTION SKID | FM |  |  |  | 251B1268 | [11 empty] | 130 GPM
GT WATER INJECTION | EX-09-1-X-01-13-033 |  | METER, FLOW - WATER INJECTION | FM2-1 | WATER INJECTION SKID | FM |  |  |  | 251B1268 | [11 empty] | 130 GPM
GT WATER INJECTION | EX-09-1-X-01-13-034 |  | FILTER, WATER INJECTION WATER | FW1-1 | WATER INJECTION SKID | FLT |  |  |  | 251B1268 |  |  | 5 MICRON
GT WATER INJECTION | EX-09-1-X-01-13-035 |  | VALVE, TRIP - WATER INJECTION STOP VALVE | VH19-1 | WATER INJECTION SKID | VLV |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-036 |  | VALVE, WATER INJECTION FLOW STAGING | VH7-1 | WATER INJECTION SKD | VLV |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-037 |  | VALVE, WATER INJECTION NOZZLE ISOLATION | VH8-1 | WATER INJECTION SKID | VLV |  |  |  | 251B1268
GT WATER INJECTION | EX-09-1-X-01-13-038 |  | REGULATOR, PRESSURE - WATER INJECTION | VPR61-1 | WATER INJECTION SKID | PR |  |  |  | 251B1268 | [13 empty] | 18 PSID
GT WATER INJECTION | EX-09-1-X-01-13-039 |  | VALVE, WATER INJECTION STOP | VS2-1 | WATER INJECTION SKID | VLV |  |  |  | 251B1268
GT WATER WASH | EX-09-1-X-01-14-001 |  | HEATER, WATER WASH PUMP MOTOR | 23TW-1 | WATER WASH PUMP MOTOR | HTR |  |  |  | 247B5538 |  |  |  |  | 60 | 1 | 120 |  | 40
GT WATER WASH | EX-09-1-X-01-14-002 |  | HEATER, IMMERSION - WATER WASH | 23WK-1 | WATER WASH TANK | HTR |  |  |  | 251B1464 |  |  |  |  | 60 | 3 | 480 |  | 50KW
GT WATER WASH | EX-09-1-X-01-14-003 |  | HEATER, IMMERSION - WATER WASH | 23WK-2 | WATER WASH TANK | HTR |  |  |  | 251B1464 |  |  |  |  | 60 | 3 | 480 |  | 50KW
GT WATER WASH | EX-09-1-X-01-14-004 |  | HEATER, IMMERSION - WATER WASH | 23WK-3 | WATER WASH TANK | HTR |  |  |  | 251B1464 |  |  |  |  | 60 | 3 | 480 |  | 50KW
GT WATER WASH | EX-09-1-X-01-14-005 |  | HEATER, WATER WASH SKID | 23WS-1 | WATER WASH SKID | HTR |  |  |  | 251B1464 |  |  |  |  | 60 | 3 | 480 |  | 25KW
GT WATER WASH | EX-09-1-X-01-14-006 |  | SWITCH, WASH WATER TEMP | 26TW-1 | WATER WASH TANK | TS |  |  |  | 251B1464 | [13 empty] | 180 DEG F
GT WATER WASH | EX-09-1-X-01-14-007 |  | SWITCH, WASH WATER TEMP | 26TW-2 | WATER WASH TANK | TS |  |  |  | 251B1464 | [13 empty] | 65 DEG F
GT WATER WASH | EX-09-1-X-01-14-008 |  | SWITCH, WASH WATER TEMP | 26TW-3 | WATER WASH TANK | TS |  |  |  | 251B1464 | [13 empty] | 52 DEG F
GT WATER WASH | EX-09-1-X-01-14-009 |  | THERMOSTAT, WATER WASH SKID VENT | 26VW-1 | WATER WASH SKID | THERMO |  |  |  | 247B5538 | [13 empty] | 95 DEG F
GT WATER WASH | EX-09-1-X-01-14-010 |  | SWITCH, WATER WASH SKID HIGH | 26VW-2 | WATER WASH SKID | TS |  |  |  | 247B5538 | [13 empty] | 130 DEG F
GT WATER WASH | EX-09-1-X-01-14-011 |  | THERMOSTAT, WATER WASH SKID HEATER | 26WS-1 | WATER WASH SKID | THERMO |  |  |  | 247B5538 | [13 empty] | 65 DEG F
GT WATER WASH | EX-09-1-X-01-14-012 |  | SWITCH, WATER WASH SKID LOW | 26WS-2 | WATER WASH SKID | TS |  |  |  | 247B5538 | [13 empty] | 43 DEG F
GT WATER WASH | EX-09-1-X-01-14-013 |  | RELAY, WATER WASH SKID TEMP ALARM | 30WWX |  | RY |  |  |  | 247B5538
GT WATER WASH | EX-09-1-X-01-14-014 |  | SWITCH, WATER TEMP SETPOINT | 43WK-1 | WATER WASH PANEL | TS |  |  |  | 251B1464
GT WATER WASH | EX-09-1-X-01-14-015 |  | SWITCH, AUTO/MANUAL OPERATION | 43WK-2 | WATER WASH PANEL | SW |  |  |  | 251B1464
GT WATER WASH | EX-09-1-X-01-14-016 |  | OVERLOAD, WATER WASH SKID HEATER | 49WS-1 | WATER WASH PANEL | OVLD |  |  |  | 247B5538
GT WATER WASH | EX-09-1-X-01-14-017 |  | SWITCH, PRESSURE - WASH WATER | 63TW-1 | WASH WATER PIPING | PS |  |  |  | 247B5538 | [13 empty] | 106 PSIG
GT WATER WASH | EX-09-1-X-01-14-018 |  | SWITCH, PRESSURE - WASH WATER, PUMP TRIP | 63TW-2 | WASH WATER PIPING | PS |  |  |  | 247B5538 | [13 empty] | 4 IN. HG
GT WATER WASH | EX-09-1-X-01-14-019 |  | LEVEL CONTROL, WASH WATER TANK | 71TW-1 | WATER WASH TANK | LC |  |  |  | 247B5538 | [13 empty] | 15 IN. WATER
GT WATER WASH | EX-09-1-X-01-14-020 |  | SWITCH, FLOW - WATER WASH SKID | 80WW1 | WASH WATER PIPING | FS |  |  |  | 251B1464 | [13 empty] | 2 GPM
GT WATER WASH | EX-09-1-X-01-14-021 |  | RELAY, WATER WASH FLOW EXISTS | 83WW |  | RY |  |  |  | 251B1464
GT WATER WASH | EX-09-1-X-01-14-022 |  | RELAY, WATER WASH PUMP TRIP | 86WWX |  | RY |  |  |  | 251B1464
GT WATER WASH | EX-09-1-X-01-14-023 |  | MOTOR, WATER WASH UNIT VENT FAN | 88VW-1 | WATER WASH SKID | MOT |  |  |  | 251B1464 |  |  |  |  | 60 | 1 | 120 |  |  | 1725 | 0.5
GT WATER WASH | EX-09-1-X-01-14-024 |  | MOTOR/PUMP ASSY, WATER WASH | 88TW-1 | WATER WASH SKID | MOT | D-1022 | MOTOR - GE, PUMP - WORTHINGTON |  | 251B1464 |  |  | 3X1X1.5X8 | 256T | 60 | 3 | 480 |  |  | 3600 | 40
GT WATER WASH | EX-09-1-X-01-14-025 |  | MOTOR, WATER WASH SKID HEATER BLOWER | 88WS-1 | WATER WASH SKID | MOT |  |  |  | 251B1464 |  |  |  |  | 60 | 3 | 480 |  |  | 1625 | 0.33
GT WATER WASH | EX-09-1-X-01-14-026 |  | LIGHT AC, WATER WASH SKID | AL-62 | WATER WASH SKID | LIGHT |  |  |  | 251B1464
GT WATER WASH | EX-09-1-X-01-14-027 |  | LIGHT AC, WATER WASH SKID | AL-63 | WATER WASH SKID | LIGHT |  |  |  | 251B1464
GT WATER WASH | EX-09-1-X-01-14-028 |  | RECEPTICLE, WATER WASH SKID | AR-50 | WATER WASH SKID | RECPT |  |  |  | 247B5538
GT WATER WASH | EX-09-1-X-01-14-029 |  | SOLENOID VALVE, WATER WASH INJECTION | 20TW-3 | WATER WASH SKID | VLV |  |  |  | 247B5538
GT WATER WASH | EX-09-1-X-01-14-030 |  | TANK, WATER WASH WATER |  | WATER WASH SKID | TNK |  | HEBELER CORP |  | 251B1464 |  | FIBERGLASS | 1500 GAL
GT WATER WASH | EX-09-1-X-01-14-031 |  | TANK, WATER WASH DETERGENT |  | WATER WASH SKID | TNK |  | HEBELER CORP |  | 251B1464 |  | FIBERGLASS | 60 GAL
GENERATOR (02) | EX-09-X-02-01-001 | 336X335 | GENERATOR |  | CTG GENERATOR COMPARTMENT | GEN | 7A4 | GE
GEN CORE COMPONENTS | EX-09-X-02-01-002 |  | HEATER, GENERATOR SPACE | 23HG-1 | GENERATOR | HTR |  |  |  | 251B1251 |  |  |  |  | 60 | 3 | 480 |  | 6.75KW
GEN CORE COMPONENTS | EX-09-X-02-01-003 |  | HEATER, GENERATOR SPACE | 23HG-2 | GENERATOR | HTR |  |  |  | 251B1251 |  |  |  |  | 60 | 3 | 480 |  | 6.75KW
GEN CORE COMPONENTS | EX-09-X-02-01-004 |  | VIBRATION SENSOR | 39V-4A | GENERATOR, TURBINE END | VIB |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-005 |  | VIBRATION SENSOR | 39V-4B | GENERATOR, TURBINE END | VIB |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-006 |  | VIBRATION SENSOR | 39V-5A | GENERATOR, EXCITOR END | VIB |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-007 |  | VIBRATION SENSOR - NON CONTACT | 39VS-101 | GENERATOR, EXCITOR END | VIB |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-008 |  | VIBRATION SENSOR - NON CONTACT | 39VS-102 | GENERATOR, EXCITOR END | VIB |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-009 |  | VIBRATION SENSOR - NON CONTACT | 39VS-91 | GENERATOR, TURBINE END | VIB |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-010 |  | VIBRATION SENSOR - NON CONTACT | 39VS-92 | GENERATOR, TURBINE END | VIB |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-011 |  | THERMOCOUPLE, BEARING METAL TEMP #1 | BT-GJ1-1A | GENERATOR BEARING #1 | TC |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-012 |  | THERMOCOUPLE, BEARING METAL TEMP #1 | BT-GJ1-1B | GENERATOR BEARING #1 | TC |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-013 |  | THERMOCOUPLE, BEARING METAL TEMP #1 | BT-GJ1-2A | GENERATOR BEARING #1 | TC |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-014 |  | THERMOCOUPLE, BEARING METAL TEMP #1 | BT-GJ1-2B | GENERATOR BEARING #1 | TC |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-015 |  | THERMOCOUPLE, BEARING METAL TEMP #2 | BT-GJ2-1A | GENERATOR BEARING #2 | TC |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-016 |  | THERMOCOUPLE, BEARING METAL TEMP #2 | BT-GJ2-1B | GENERATOR BEARING #2 | TC |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-017 |  | THERMOCOUPLE, BEARING METAL TEMP #2 | BT-GJ2-2A | GENERATOR BEARING #2 | TC |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-018 |  | THERMOCOUPLE, BEARING METAL TEMP #2 | BT-GJ2-2B | GENERATOR BEARING #2 | TC |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-019 |  | TEMPERATURE ELEMENT, COLD GAS | DT-GGC-10 | GENERATOR, TURBINE END | TE |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-020 |  | TEMPERATURE ELEMENT, COLD GAS | DT-GGC-11 | GENERATOR, EXCITOR END | TE |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-021 |  | TEMPERATURE ELEMENT, HOT GAS | DT-GGH-18 | GENERATOR, TURBINE END | TE |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-022 |  | TEMPERATURE ELEMENT, HOT GAS | DT-GGH-19 | GENERATOR, EXCITOR END | TE |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-023 |  | TEMPERATURE ELEMENT, STATOR | DT-GSA-4/R | GENERATOR, EXCITOR END | TE |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-024 |  | TEMPERATURE ELEMENT, STATOR | DT-GSA-5/R | GENERATOR, EXCITOR END | TE |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-025 |  | TEMPERATURE ELEMENT, STATOR | DT-GSA-5/R | GENERATOR, EXCITOR END | TE |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-026 |  | TEMPERATURE ELEMENT, STATOR | DT-GSF-1/R | GENERATOR, TURBINE END | TE |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-027 |  | TEMPERATURE ELEMENT, STATOR | DT-GSF-2/R | GENERATOR, TURBINE END | TE |  |  |  | 251B1251
GEN CORE COMPONENTS | EX-09-X-02-01-028 |  | TEMPERATURE ELEMENT, STATOR | DT-GSF-3/R | GENERATOR, TURBINE END | TE |  |  |  | 251B1251
GEN LUBE OIL | EX-09-X-02-02-001 |  | SWITCH, LUBE OIL PRESSURE LOW TRIP | 63QT-2A | GENERATOR COMPARTMENT | PS |  |  |  | 251B1251 | [13 empty] | 8 PSIG
GEN LUBE OIL | EX-09-X-02-02-002 |  | SWITCH, LUBE OIL PRESSURE LOW TRIP | 63QT-2B | GENERATOR COMPARTMENT | PS |  |  |  | 251B1251 | [13 empty] | 8 PSIG
GEN LUBE OIL | EX-09-X-02-02-003 |  | THERMOCOUPLE, LUBE OIL TEMP | LT-G1D-1A | GENERATOR BEARING #1 DRAIN | TC |  |  |  | 251B1251
GEN LUBE OIL | EX-09-X-02-02-004 |  | THERMOCOUPLE, LUBE OIL TEMP | LT-G1D-1B | GENERATOR BEARING #1 DRAIN | TC |  |  |  | 251B1251
GEN LUBE OIL | EX-09-X-02-02-005 |  | THERMOCOUPLE, LUBE OIL TEMP | LT-G2D-1A | GENERATOR BEARING #2 DRAIN | TC |  |  |  | 251B1251
GEN LUBE OIL | EX-09-X-02-02-006 |  | THERMOCOUPLE, LUBE OIL TEMP | LT-G2D-1B | GENERATOR BEARING #2 DRAIN | TC |  |  |  | 251B1251
BALANCE OF PLANT (04)
LIQUID FUEL FORWARDING | EX-09-X-04-01-001 |  | VALVE, LIQUID FUEL STOP | 20FD-1 | FUEL SUPPLY LINE | VLV | 609GWA96DCLC | LAURENCE |  | 251B1181 |  |  | 3"
LIQUID FUEL FORWARDING | EX-09-X-04-01-002 |  | HEATER, FUEL | 23FH-1 | FUEL FORWARDING SKID | HTR | NWHO-90155E4VXX | CHROMOLOX |  | 251B1181 |  |  |  |  | 60 | 3 | 480 |  | 105 KW
LIQUID FUEL FORWARDING | EX-09-X-04-01-003 |  | HEATER, FUEL | 23FH-2 | FUEL FORWARDING SKID | HTR | NWHO-90155E4VXX | CHROMOLOX |  | 251B1181 |  |  |  |  | 60 | 3 | 480 |  | 105 KW
LIQUID FUEL FORWARDING | EX-09-X-04-01-004 |  | SWITCH, FUEL TEMP | 26FD-1 | FUEL FORWARDING SKID | TS |  | FENWELL | 17002-0 | 251B1181 | [13 empty] | 150 DEG F
LIQUID FUEL FORWARDING | EX-09-X-04-01-005 |  | THERMOSTAT, FUEL HEATER | 26FH-1 | FUEL FORWARDING SKID | THERMO |  |  |  | 251B1181
LIQUID FUEL FORWARDING | EX-09-X-04-01-006 |  | THERMOSTAT, FUEL HEATER | 26FH-2 | FUEL FORWARDING SKID | THERMO |  |  |  | 251B1181
LIQUID FUEL FORWARDING | EX-09-X-04-01-007 |  | SWITCH, FUEL PRESSURE | 63FD-2 | FUEL FORWARDING SKID | PS | 100P42C3A | NEO-DYN |  | 251B1181 | [13 empty] | 60 PSIG
LIQUID FUEL FORWARDING | EX-09-X-04-01-008 |  | SWITCH, FUEL FILTER DIFF PRESSURE | 63LF-2 | FUEL FORWARDING SKID | PS |  |  |  | 251B1181 | [13 empty] | 5 PSID
LIQUID FUEL FORWARDING | EX-09-X-04-01-009 |  | MOTOR/PUMP ASSY, FUEL FORWARDING | 88FD-1 | FUEL FORWARDING SKID | MOT | 2X1X10 HOC2 | INGERSOLL-RAND |  | 251B1181 |  |  |  |  | 60 | 3 | 460 |  |  | 3600 | 25 | 165 GPM
LIQUID FUEL FORWARDING | EX-09-X-04-01-010 |  | MOTOR/PUMP ASSY, FUEL FORWARDING | 88FD-2 | FUEL FORWARDING SKID | MOT | 2X1X10 HOC2 | INGERSOLL-RAND |  | 251B1181 |  |  |  |  | 60 | 3 | 460 |  |  | 3600 | 25 | 165 GPM
LIQUID FUEL FORWARDING | EX-09-X-04-01-011 |  | FLOW METER | FM-1 | FUEL FORWARDING SKID | FM | B62-DB | BROOKS INSTRUMENT, EMERSON ELECTRIC |  | 251B1181
LIQUID FUEL FORWARDING | EX-09-X-04-01-012 |  | REGULATOR, FUEL PRESSURE | VPR53-1 | FUEL FORWARDING SKID | PR | 655ED | FISHER |  | 251B1181 | [13 empty] | 85 PSIG
LIQUID FUEL FORWARDING | EX-09-X-04-01-013 |  | VALVE, RELIEF - FUEL HEATER | VR51-1 | FUEL FORWARDING SKID | RV |  | NUPRO | SS-8-CPA2-50 | 251B1181 | [13 empty] | 145 PSIG
LIQUID FUEL FORWARDING | EX-09-X-04-01-014 |  | STRAINER, FUEL |  | FUEL FORWARDING SKID | STR | 50 DUPLEX | HAYWARD |  | 251B1181 |  | STEEL | 4"
COOLING WATER | EX-09-X-04-04-001 |  | SWITCH, COOLING FAN VIBRATION | 39FC-1 | FIN FAN COOLER FANS | VS |  |  |  | 251B1653
COOLING WATER | EX-09-X-04-04-002 |  | SWITCH, COOLING FAN VIBRATION | 39FC-2 | FIN FAN COOLER FANS | VS |  |  |  | 251B1653
COOLING WATER | EX-09-X-04-04-003 |  | SWITCH, COOLING WATER PRESSURE | 63WC-1 | COOLING WATER PUMP DISCHARGE | PS |  |  |  | 251B1653 | [13 empty] | 56 PSIG
COOLING WATER | EX-09-X-04-04-004 |  | SWITCH,COOLING WATER LEVEL | 71WL-1 | COOLING WATER EXPANSION TANK | LS |  |  |  | 251B1653
COOLING WATER | EX-09-X-04-04-005 |  | FAN/MOTOR ASSY, COOLING WATER | 88FC-1 | FIN FAN COOLER | MOT | 5400 | MOTOR - GE, FAN - ECODYNE |  | 251B1653 |  |  | 9' DIA. 6 BLADE | 286T | 60 | 3 | 480 |  |  | 900 | 10
COOLING WATER | EX-09-X-04-04-006 |  | FAN/MOTOR ASSY, COOLING WATER | 88FC-2 | FIN FAN COOLER | MOT | 5400 | MOTOR - GE, FAN - ECODYNE |  | 251B1653 |  |  | 9' DIA. 6 BLADE | 286T | 60 | 3 | 480 |  |  | 900 | 10
COOLING WATER | EX-09-X-04-04-007 |  | PUMP/MOTOR ASSY, COOLING WATER | 88WC-1 |  | MOT | 8011 | MOTOR - GE, PUMP - BUFFALO PUMPS |  | 251B1653 |  |  |  | 365TS | 60 | 3 | 480 |  |  | 1800 | 75
COOLING WATER | EX-09-X-04-04-008 |  | PUMP/MOTOR ASSY, COOLING WATER | 88WC-2 |  | MOT | 8011 | MOTOR - GE, PUMP - BUFFALO PUMPS |  | 251B1653 |  |  |  | 365TS | 60 | 3 | 480 |  |  | 1800 | 75
COOLING WATER | EX-09-X-04-04-009 |  | REGULATOR VALVE, ATMG AIR PRECOOLER AIR DISCHARGE TEMP | VTR2-1 | PRECOOLER DISCHARGE | TR | RT-1010-A2 | ROBERTSHAW |  | 251B1653 | [13 empty] | 225 DEG F
COOLING WATER | EX-09-X-04-04-010 |  | REGULATOR VALVE, LUBE OIL HEAT EXCHG TEMP | VTR1-1 | OIL HEAT EXCHG DISCHARGE | TR | RT-1010-A2 | ROBERTSHAW |  | 251B1653 | [13 empty] | 130 DEG F