## PM
MANUFACTURE | DESCRIPTION | FREQUENCY | NEXT DUE DATE | CRAFT ID | EST Duration / HRS | EQUIP ID | PROCEDURE NUMBER |  | STATUS
GE | Borescope Inspection | 6 Months |  |  | 12 |  | PM-501 | Comp
GE | Combustion Inspection | 800 Fired Starts |  |  | 64 |  | PM-502 | Comp
GE | Hot Gas Path Inspection | 1200 Fired Starts |  |  | 160 |  | PM-503 | Comp
GE | Major Inspection | 2400 Fired Starts |  |  | 320 |  | PM-504 | Comp
GE | Accessory Gear Coupling Inspection | 3 Years |  |  | 3 |  | PM-505
GE | Starting Motor, Lubricate | 1 Year |  |  | 1 |  | PM-585 | Comp
GE | Starting Motor Coupling, Lubricate | 1 Year |  |  | 1 |  | PM-505
GE | Starting Motor, Remove and Conduct Internal Inspection | 5 Years |  |  | 16 |  | PM-508
GE | Turning Gear Motor Lubricate | 7 Years |  |  | 1 |  | PM-585 | Comp
Buffalo Forge | Aux Lube Oil Pump, Lubricate | 1 Year |  |  | 1 |  | PM-586 | Comp
Buffalo Forge | Emergency Lube Oil Pump, Lubricate | 1 Year |  |  | 1 |  | PM-586 | Comp
Buffalo Forge | Cooling Water Pumps, Lubricate | 6 Months |  |  | 0.5 |  | PM-586 | Comp
GE | Cooling Water Pump Motors, Lubricate | 6 Months |  |  | 0.5 |  | PM-585 | Comp
Buffalo Forge | Cooling Water Pump Couplings, Lubricate | 6 Months |  |  | 0.5 |  | PM-505
GE | Cooling Water Fan Motors, Lubricate | 6 Months |  |  | 1 |  | PM-585 | Comp
GE | Cooling Water Fan Pillow Blocks, Lubricate | 6 Months |  |  | 1 |  | PM-516
Turbonetics | Atomizing Air Compressor Coupling, Lubricate | 1 Year |  |  | 0.5 |  | PM-505
Turbonetics | Atomizing Air Compressor Motor, Lubricate | 6 Months |  |  | 0.5 |  | PM-585 | Comp
GE | Aux Hydraulic Pump Motor, Lubricate | 7 Years |  |  | 0.5 |  | PM-585 | Comp
GE | VIGV Ring, Gears, Linkage, Lubricate | 6 Months |  |  | 1 |  | PM-520
GE | Exhaust Frame Cooling Fan Motors, Lubricate | 6 Months |  |  | 1 |  | PM-585 | Comp
GE | Compressor Extraction Air Solenoid Valve Plunger, Lubricate | 6 Months |  |  | 0.5 |  | PM-522
GE | Compartment Space Heater Fan Motors, Lubricate | 1 Year |  |  | 1 |  | PM-585 | Comp
GE | Compartment Vent Fan Motors, Lubricate | 6 Months |  |  | 1 |  | PM-585 | Comp
GE | Fuel Forwarding Pump Motors, Lubricate | 1 Year |  |  | 1 |  | PM-585 | Comp
GE | Water Injection Pump Motor, Lubricate | 1 Year |  |  | 1 |  | PM-585 | Comp
Envirotech | Water Injection Pump, Lubricate | 1 Year |  |  | 1 |  | PM-586 | Comp
GE | Water Wash Pump Motor, Lubricate | 1 Year |  |  | 1 |  | PM-585 | Comp
Worthington | Water Wash Pump, Lubricate | 1 Year |  |  | 0.5 |  | PM-586 | Comp
GE | Enclosure Inspection | 6 Months |  |  | 0.5 |  | PM-530 | Comp
GE | Vibration System Check | 6 Months |  |  | 1.5 |  | PM-531 | Comp
GE | Lube Oil System Test | 6 Months |  |  | 3 |  | PM-532
GE | Liquid fuel filter inspection | 1 Year |  |  | 2 |  | PM-533
GE | Ignition System Check | 6 Months |  |  | 2 |  | PM-534 | Comp
GE | Igniter Plug Inspection | 6 Months |  |  | 2 |  | PM-535 | Comp
GE | Fuel Metering Valve Check | 6 Months |  |  | 2 |  | PM-536 | Comp
GE | Fuel Shutoff Valves, Check | 6 Months |  |  | 2 |  | PM-537 | Comp
GE | Fuel Purge and Solenoid Valve Check | 6 Months |  |  | 2 |  | PM-538 | Comp
GE | Exhaust Plenum, Inspect | 6 Months |  |  | 3 |  | PM-539 | Comp
GE | External Engine Inspection and Cleaning | 6 Months |  |  | 2 |  | PM-540 | Comp
GE | Calibrate Temp Setpoints | 1 Year |  |  | 1 |  | PM-542 | Comp
| Pressure Gauges, Calibrate | 1 Year |  |  | 1 |  | PM-543 | Comp
| Flow meters, Calibrate | 1 Year |  |  | 1 |  | PM-545 | Comp
| Generator Panel Meters, Calibrate | 1 Year |  |  | 1 |  | PM-546
| Pressure Regulating Valves, Inspect | 1 Year |  |  | 1 |  | PM-549
| Temperature Regulating Valves, Inspect | 1 Year |  |  | 1 |  | PM-550
| Gas/Liquid Strainers, Clean and Inspect | 1 Year |  |  | 3 |  | PM-553
| Lube Oil Filters, Clean/Replace | 1 Year or 15 PSID |  |  | 2 |  | PM-553
Hilliard | Fuel Filters, Clean/Replace | 1 Year or 15 PSID |  |  | 2 |  | PM-553
| Hydraulic Supply Filter, Clean Replace | 1 Year or 60 PSID |  |  | 2 |  | PM-553
Friedrich | Air Conditioner Filter, Clean/Inspect | 6 Months |  |  | 1 |  | PM-557
| Lube Oil Sample/Analysis | 6 Months |  |  | 0.5 |  | PM-558 | Comp
| Heat Exchangers, Clean/Inspect | 3 Years |  |  | 5 |  | PM-559
| Cooling Water Fin Fan Cooler, Clean/Inspect | 1 Year |  |  | 6 |  | PM-560 | Comp
| Main Fuel Pump, Inspect | 1 Year |  |  | 3 |  | PM-561
| Fuel Flow Divider, Inspect | 1 Year |  |  | 2 |  | PM-562
| Fuel Flow Divider, Drain and Install Corrosion Inhibitor | 1 Year |  |  | 3 |  | PM-563
| Fuel Flow Divider Speed Pickups, Inspect/Gap | 1 Year |  |  | 3 |  | PM-564
| False Start Drain Valves, Inspect | 1 year |  |  | 1 |  | PM-565
GE Speedtronics Control System | Calibrate FSR verses Fuel Flow LVDT's | 1 Year |  |  | 2 |  | PM-566
GE Speedtronics Control System | Electronic Trip Actuation of 20 FL and 20 HD | 1 Year |  |  | 1 |  | PM-567
GE Speedtronics Control System | Check 20 FL Operation | 1 Year |  |  | 1 |  | PM-568
GE Speedtronics Control System | LVDT Feedback at Firing Speed verses FSR | 1 Year |  |  | 2 |  | PM-569
GE Speedtronics Control System | Calibrate FSR verses Gas Control Valve Stroke | 1 Year |  |  | 2 |  | PM-570
GE Speedtronics Control System | P2 Transducer Calibration | 1 Year |  |  | 1 |  | PM-571
GE Speedtronics Control System | LVDT Calibration | 1 Year |  |  | 1 |  | PM-572
| Gas Control Valve, Inspect for Leaks | 1 Month |  |  | 1 |  | PM-573
| Gas Control Valve, Inspect Valve Plug and Seat | At Major Inspection |  |  | 4 |  | PM-574
GE | VIGV Bushing Inspection | At CI, Hot Gas Path, Major Inspection |  |  | 4 |  | PM-575
GE | VIGV Calibration | 1 Year |  |  | 3 |  | PM-576
GE | VIGV, Inspect For Hydraulic System Leaks | 1 Month |  |  | 1 |  | PM-577
GE | Compartment Fire Detectors, Inspect for Proper Operation | 1 Year |  |  | 1 |  | PM-578 | Comp
Donaldson | Inspect Inlet Air Filters, Change Sock Filter | 1 Year |  |  | 2 |  | PM-579 | Comp
Safety Valves | Test | 1 Year |  |  | 1.5 |  | PM-581 | Comp
Transformer | Oil Test | 1 Year |  |  | 1 |  | PM-582 | Comp
Beckwith Gen Protection | Test | 1 Year |  |  | 3 |  | PM-584 | Comp
Goulds Motors | Lubricate | 6 Months |  |  | 1 |  | PM-585 | Comp
Goulds Pumps | Lubricate | 6 Months |  |  | 1 |  | PM-586 | Comp
ITT Neo Dyn Pressure Switch | Calibrate | 1 Year |  |  | 1 |  | PM-587 | Comp
ITT Neo Dyn Temperature Switch | Calibrate | 1 Year |  |  | 1 |  | PM-588 | Comp
Rosemount Pressure Transmitters | Calibrate | 1 Year |  |  | 1 |  | PM-589 | Comp
Battery | Electrolyte Level Check | 30 Days |  |  | 0.5 |  | PM-590 | Comp
Battery | Check Connectors | 1 Year |  |  | 0.5 |  | PM-591 | Comp
Voith Pump | Inspect, Clean Filter | 3 Months |  |  | 0.5 |  | PM-592 | Comp
C02 Storage | Annual Inspection | 1 Year |  |  | 2 |  | PM-593 | Comp
Voith Pump | Change oil | 1 Year |  |  | 1 |  | PM-594 | Comp
Gas Detector | Calibrate | 1 Year |  |  | 1 |  | PM-595 | Comp
CO2 System | Test | 1 Year |  |  | 3 |  | PM-596 | Comp
CO2 System | Hydrostatic Test | 1 Year |  |  | 1 |  | PM-597 | Comp
Air/Oil Separator | Filter Check | 6 Months |  |  | 3 |  | PM-598 | Comp
Evap Cooling | Pre-winter Checks | 1 Year |  |  | 3 |  | PM-599 | Comp
480 VAC Breaker | Inspection and Clean | 1 Year |  |  | 5 |  | PM-606 | Comp
Heat Trace | Inspection | 1 Year |  |  | 4 |  | PM-607
13kV Breaker | Inspection | 1 Year |  |  | 5 |  | PM-608 | Comp
CEM | Weekly Maintenance | 1 Week |  |  | 1 |  | PM-609 | Comp
CEM | Monthly Maintenance | 30 Days |  |  | 2 |  | PM-610 | Comp
Control Panels | Clean/Inspect | 6 Months |  |  | 2 |  | PM-611 | Comp
Plant | Vibration Analysis | 3 Months |  |  |  |  | PM-612 | Comp
Plant | Infrared Thermography | 6 Months |  |  |  |  | PM-613 | Comp