Borescope Inspection

7EA Gas Turbine

PSEG Power

Table of Contents

Purpose:	2

OEM Recommendations:	2

Resources Required:	2

Precautions and Limitations:	2

Pre-Job Preparation / Requirements:	3

Procedure Steps:	3

Post Job Requirements:	18

Reference Documents:	18

Materials:	18

Tools:	18

Attachments Table of Contents	18

Materials Request Form	18

Tooling Request Form	18

Lock Out/Tag Out Authorization Form	18

PSEG Standard Report Form	18

# Purpose:

The gas turbine incorporates provisions in both turbine and compressor casings for visual inspection of an intermediate compressor rotor stage or stages, first- and second-stage turbine buckets and nozzle partitions by means of the optical borescope.

These provisions, consisting of radially aligned holes through the casings and internal stationary turbine shrouds, are designed to allow the penetration of an optical borescope into the gas- or air-flow path regions of a non-operating gas turbine. Optical borescopes are utilized to provide visual inspection of the rotating and stationary parts without removing the upper compressor and turbine casings.

The application of a monitoring program, utilizing the borescope, will allow scheduling outages and pre-planning of parts requirements, resulting in lower maintenance costs, higher availability and reliability of the gas turbine.

# OEM Recommendations:

- The gas turbine must be shut down and the turbine wheelspace temperatures no greater than 180°F (82°C) before the borescope is inserted.

Station Requirements:

- The gas turbine must be shut down and the turbine wheelspace temperatures no greater than 100°F before the borescope is inserted. Exposure of the borescope to higher temperatures may permanently damage the internal glass fiber optical cable.  The 2nd stage wheel space temperature should be monitored because it retain the most heat the longest amount of time.

# Resources Required:

- GE Company Field Service Representative.

- Qualified Mechanical Technician (MO).

- Third Party Contractor.

# Precautions and Limitations:

- Comply with the Lockout/Tagout program associated with this system.

- The gas turbine must be shut down and the turbine wheelspace temperatures no greater than 100°F before the borescope is inserted.

# Pre-Job Preparation / Requirements:

- Abide by all safety policies and procedures.

- MS-7001E/EA Borescope Access Hole Locations (See Table Below)

| Identification | Location | Number of Holes |
| --- | --- | --- |
| Fourth-Stage Compressor | 30.40″(77.2 cm) Aft from Forward Flange Face of the Forward Compressor Case | 2 |
| Twelfth-Stage Compressor | 5.105″(12.9 cm) Aft from Forward Flange Face of the Compressor Dis-charge Case | 2 |
| Seventeenth-Stage Compressor | 29.635″(75.3 cm) Aft from Forward Flange Face of the Compressor Dis-charge Casing | 2 |
| First-Stage Nozzle Trailing Edge | 8.88″(22.6 cm) Aft from Forward | 8 |
| & First Stage Bucket Leading Edge | Flange Face of the Turbine Casing |  |
| First-Stage Bucket Trailing Edge | 12.30″(31.2 cm) Aft from Forward | 1 |
| & Second Stage Nozzle Leading Edge | Flange Face of the Turbine Casing |  |
| Second-Stage Bucket Leading Edge | 22.97″(57.1 cm) Aft from Forward | 4 |
| & Second Stage Nozzle Trailing Edge | Flange Face of the Turbine Casing |  |
| Second-Stage Bucket Trailing | 26.48″(67.3 cm) Aft from Forward | 1 |
| & Third Stage Nozzle Leading Edge | Flange Face of the Turbine Casing |  |
| Third-Stage Bucket Leading Edge | 37.19″(94.5 cm) Aft from Forward | 4 |
| & Third Stage Nozzle Trailing Edge | Flange Face of the Turbine Casing |  |

# Procedure Steps:

Note:

All casing holes on the MS-7001 have an inner plug beneath the threaded plug in the casings. Both plugs must be removed to gain access. Ensure that inner plugs are correctly replaced after completing inspection.

- Complete all prerequisites.

- Complete Safety briefing.

- Note:

- When inspecting compressor blades and turbine buckets, it is necessary to rotate the rotor incrementally to bring each bucket into the field of view of the borescope. Withdraw the borescope slightly while turning the rotor to prevent damage to the equipment.

- Caution

- A lube oil supply to the rotor bearings must be maintained during the borescope inspection.

- Mark the load coupling.  A “zero” datum should be established for the rotor by marking the load coupling. This will provide the necessary reference to determine one revolution or intermediate angular positions.

- Open the 2 access ports at the 4th stage compressor section.  This will give access to the 3rd, 4th, 5th stage vanes and blades.

- Insert  the borescope, the light switched ON and the light intensity adjusted.

- Note:

- If the turbine internal parts are abnormally dirty, (ingested dirt or oil vapors) the turbine should be cleaned before proceeding with the borescope inspection.

- Visually inspect all visible stationary vane/blade at each visible stage from root to tip including platforms.

4th Stage Blades

- Inspect compressor components for foreign object damage, dirt build-up, corrosion, tip erosion, trailing edge thinning, stator blade root erosion, tip clearance. See chart below for limits.

4th Stage Stator Vanes

- Ensure that all sealing plugs at borescope access holes are lubricated, replaced and tightened upon completion of the inspection.

- Open the 2 access ports at the 12th stage compressor section.  This will give access to the 11th, 12th, 13th stage vanes and blades.

- Insert the borescope, the light switched ON and the light intensity adjusted.

- Visually inspect all visible stationary vane/blade at each visible stage from root to tip including platforms.

- Inspect compressor components for foreign object damage, dirt build-up, corrosion, tip erosion, trailing edge thinning, stator blade root erosion, tip clearance. See chart below for limits.

- Ensure that all sealing plugs at borescope access holes are lubricated, replaced and tightened upon completion of the inspection.

- Open the 2 access ports at the 17th stage compressor section.  This will give access to the trailing edge of the 17th stage buckets.

- Insert the borescope, the light switched ON and the light intensity adjusted.

- Visually inspect all visible stationary vane/blade at each visible stage from root to tip including platforms.

- Inspect compressor components for foreign object damage, dirt build-up, corrosion, tip erosion, trailing edge thinning, stator blade root erosion, tip clearance. See chart below for limits.

- Ensure that all sealing plugs at borescope access holes are lubricated, replaced and tightened upon completion of the inspection.

- Open the combustor via the spark igniters and the flame detectors.  This will give access to the combustion liners, transition pieces and crossover tubes.

- Insert the borescope, the light switched ON and the light intensity adjusted.

Combustor Liner Cap

- Inspect combustion liners, transition pieces and cross over tubes for carbon build-up, hot spots, cracking, bulging, wear, missing metal.

Fuel Nozzle Swirler

Transition Piece

Crossfire tube

- Ensure that all sealing plugs at borescope access holes are lubricated, replaced and tightened upon completion of the inspection.

- Open the 8 access ports at the turbine section.  This will give acces to the trailing edge of the 1st stage nozzles and the leading edge of the 1st stage buckets.

- Insert  the borescope, the light switched ON and the light intensity adjusted.

- Visually inspect all visible stationary bucket/blade at each visible stage from root to tip including platforms and tip seals.

- Inspect turbine nozzles for foreign object damage, corrosion, blocked cooling holes, cracks, trailing edge bowing, erosion, burning. See chart below for limits.

1st Stage Nozzle

- Inspect turbine buckets for foreign object damage, corrosion, blisters, erosion, cracks, tip clearance, missing metal. See chart below for limits.

1st Stage Leading Edge Bucket

First Stage Bucket Limits

Cracks — Cracks on first-stage buckets are unacceptable with one exception: radial cracks on the bucket squealer tip less than 0.3 inch (0.8 cm) long are permissible. These cracks usually occur as a result of foreign object damage. Radial cracks in certain areas of the squealer tip may be remedied by removing material. The limits are covered in paragraph Missing Metal.

Dents — Dents are permissible with the following limits:

The dent must not contain any cracks per the above paragraph.

The dent must not obstruct the diameter of or penetrate into a cooling air hole. The cooling hole closest to the leading edge should pass a 0.091-inch- (0.23-cm-) diameter wire or 3/32- inch (0.24-cm) ball to be acceptable. Holes 2 through 12 must pass a 0.072-inch- (0.18-cm-) diameter wire or a 1/16-inch (0.16-cm) ball to be acceptable. The trailing edge hole must pass a 0.051-inch- (0.13-cm-) diameter wire or 3/64-inch (0.12-cm) ball to be acceptable.

A dent must not be more than 0.125 inch (0.32 cm) deep. Therefore in areas where metal thickness to a cooling hole is not the limiting factor, a dent may be blended to remove resulting cracks or metal displacement, provided the 0.125-inch (0.32-cm) limit is not exceeded.

Missing Metal — Missing metal on first-stage buckets occurring in the squealer portion can be repaired by blending. Missing metal or radial cracks in the squealer portions can be corrected within the following limits:

The squealer tip wall may be removed for a surface distance of 1.5 inches (3.81 cm) from the leading edge on the suction side of the bucket.

The squealer tip wall may be removed for a surface distance of 0.75 inch (1.91 cm) from the leading edge on the pressure side of the bucket. See Figure HGP-I.15, Squealer Tip Repair Limit.

Missing metal, dents and blending of cracks in the leading edge must not extend more than 1.125 inches (2.86 cm) down from the top edge of the bucket. No more than five buckets total may have leading edge blending below the squealer section without a resultant loss in performance.

Corrosion — First-stage buckets are more susceptible to damage by corrosion, erosion and oxidation than second- or third-stage buckets. This condition usually first appears on the leading edge of the airfoil as a flattening and roughening of the surface; however, the entire airfoil is susceptible to corrosion, erosion or oxidation attack.

Direct measurement of this wearing is difficult, if not impossible; however, general criteria can be established. The cooling hole closest to the leading edge is approximately 0.25-inch (6.3mm) from the leading edge and about 0.8 inch (2.03 cm) from the airfoil suction side surface. The corrosion pattern on the leading edge will allow a maximum of 0.070 inch (0.18 cm) corrosion before a breakdown of the hole closest to the leading edge occurs. This break- down appears as a depression on the suction side surface, near the leading edge. If this condition appears on the first-stage buckets, replacement is required.

If some lesser amount of corrosion is observed, judgment is required to weigh the possibility of a corrosion-related failure against the cost of replacement of buckets at the time of inspection.

Realize the 0.125 inch (0.32 cm) of corrosion constitutes a total corrosion life. The fraction of 0.125 inch (0.32 cm) removed is the fraction of the life used. (It is assumed that corrosion progresses linearly with time.) Replace the buckets if total corrosion life is predicted before the next planned inspection.

- Ensure that all sealing plugs at borescope access holes are lubricated, replaced and tightened upon completion of the inspection.

- Open the 1 access ports at the turbine section.  This will give access to the trailing edge of the 1st stage buckets and the leading edge of the 2nd stage nozzles.

- Insert  the borescope, the light switched ON and the light intensity adjusted.

- Visually inspect all visible stationary bucket/blade at each visible stage from root to tip including platforms and tip seals.

- Inspect turbine nozzles for foreign object damage, corrosion, blocked cooling holes, cracks, trailing edge bowing, erosion, burning. See chart below for limits.

- Inspect turbine buckets for foreign object damage, corrosion, blisters, erosion, cracks, tip clearance, missing metal. See chart above for limits.

- Ensure that all sealing plugs at borescope access holes are lubricated, replaced and tightened upon completion of the inspection.

- Open the 4 access ports at the turbine section.  This will give access to the trailing edge of the 2nd stage nozzles and the leading edge of the 2nd stage buckets.

- Insert  the borescope, the light switched ON and the light intensity adjusted.

2nd Stage Leading Edge Bucket, 2nd Stage Trialing Edge Nozzle

- Visually inspect all visible stationary bucket/blade at each visible stage from root to tip including platforms and tip seals.

- Inspect turbine nozzles for foreign object damage, corrosion, blocked cooling holes, cracks, trailing edge bowing, erosion, burning. See chart below for limits.

- Inspect turbine buckets for foreign object damage, corrosion, blisters, erosion, cracks, tip clearance, missing metal. See chart below for limits.

Second and Third Stage Bucket Limits

Cracks — Cracks also occur in the second- and third-stage buckets due to foreign object damage.

These cracks usually occur at the airfoil leading edge in the outer span sections.

Second- and third-stage bucket cracks are repairable if located in the outer one-third (1/3) of the airfoil and up to 0.35 inch (0.89 cm) in length.

These cracks can be repaired by blending the airfoil in the area of the crack while maintaining radii at all intersection points. The leading-edge radius must not be retained in the repaired area.

Missing Metal — Missing material in the second- and third-stage buckets is acceptable if the airfoil can be contoured to the same limits as the crack repair.

Dents — Dents are acceptable, as long as the dent is not located in the bucket root fillet (interface between airfoil and platform) or in the shroud fillet (interface between airfoil and shroud).

Dents containing cracks or those located in the shroud fillet are repairable. Repairable dents should be hand polished to remove foreign material in the area of the dent and fluorescent penetrant inspected for cracks. Blend smooth all dents.

Air-cooled second-stage buckets must pass a 0.057-inch- (0.14-cm-) diameter wire through all eight holes from the bucket tip to beyond the platform. An additional check should be made to ensure that the passageway through the bucket shank is open and clear.

Corrosion on second- and third-stage buckets to a depth of more than 0.025 inch (0.06 cm) has not been observed. Such a condition is acceptable. If a more serious corrosion is noted, the observations should be reported to the responsible General Electric Company Field Service Representative.

- Ensure that all sealing plugs at borescope access holes are lubricated, replaced and tightened upon completion of the inspection.

- Open the 1 access ports at the turbine section.  This will give access to the trailing edge of the 2nd stage buckets and the leading edge of the 3rd stage Nozzles.

- Insert  the borescope, the light switched ON and the light intensity adjusted.

- Visually inspect all visible stationary bucket/blade at each visible stage from root to tip including platforms and tip seals.

- Inspect turbine nozzles for foreign object damage, corrosion, blocked cooling holes, cracks, trailing edge bowing, erosion, burning. See chart above for limits.

- Inspect turbine buckets for foreign object damage, corrosion, blisters, erosion, cracks, tip clearance, missing metal. See chart above for limits.

- Ensure that all sealing plugs at borescope access holes are lubricated, replaced and tightened upon completion of the inspection.

- Open the 4 access ports at the turbine section.  This will give access to the trailing edge of the 3rd stage nozzles and the leading edge of the 3rd stage buckets.

- Insert  the borescope, the light switched ON and the light intensity adjusted.

- Visually inspect all visible stationary bucket/blade at each visible stage from root to tip including platforms and tip seals.

3rd Stage Leading Edge Bucket, 3rd Stage Trialing Edge Nozzle

- Inspect turbine nozzles for foreign object damage, corrosion, blocked cooling holes, cracks, trailing edge bowing, erosion, burning. See chart above for limits.

- Inspect turbine buckets for foreign object damage, corrosion, blisters, erosion, cracks, tip clearance, missing metal. See chart above for limits.

3rd Stage Trialing Edge Bucket as seen through the Exhaust Duct

- Ensure that all sealing plugs at borescope access holes are lubricated, replaced and tightened upon completion of the inspection.

# Post Job Requirements:

Down load any digital pictures to be placed into the final borescope report.  The borescope findings should be place into a formal report and given to the Maintenance Manager.

# Reference Documents:

- GEK 104051

# Materials:

- Standard Borescope report form

- Materials Request Form

- Tooling Request Form

- Lock Out/Tag Out Authorization Form

# Tools:

- Rigid borescope

- Flexible fiberoptic borescope

- Borescope Light Source

- Camera attachments, camera, and/or a television camera with recording capability and playback monitor.

- Standard Tools for removal of Borescope port plugs

**End of Procedure**

# Attachments Table of Contents

## Materials Request Form

## Tooling Request Form

## Lock Out/Tag Out Authorization Form

## PSEG Standard Report Form