SECTION 4  	DESIGN CONDITIONS

4.1	Design Basis

| Design Conditions | 2 x Fr 7FA |
| --- | --- |
| Site Elevation | 732 ft. |
| Average Temperature | 80ºF |
| Relative Humidity Average annual precipitation Seismic Zone | 77 % 50.3 in. 4 |
| Wind Speed | 75 mph |
| Minimum Gas Pressure | 247 psig |
| Plant Fuel Consumption Rate (2) Frame 7FA | 84 MCFD Natural Gas* |
| High Voltage Interconnect | 18KV Terminals of 18KV/230 KV GSU’s |
| Demin Water Storage Demin Water Required | 5,000 Gallon SS Tank by Contractor 15 gpm per GTG water wash only |
| Instrument Air System | 185 SCFM by Contractor |
| Waste Oil Storage | 10,000 Gallons by Contractor |
| Waste Water | Pump to Owner for disposal |
| Raw/Firewater Water Storage | 264,000 Gallon CS Tank Existing |

Diesel Tank                                                                            5,000 Gallon

Diesel Fueled Emergency Generator                                500 KW

R.O. Water Storage Tank			          3,000 Gallon

*assumes 900 – 1050 Btu/Scf natural gas quality

  - Interconnect Points

| Natural Gas at min. 247 psig | Owner to provide interconnection point to the Plant Battery Limits. |
| --- | --- |
| Plant Waste Water | Owners water disposal. |
| Plant Waste Oil | Owners Truck disposal |
| 18 KV | Frame 7FA GSU terminals adjacent to plant |
| Telephone | Plant Battery Limits by Owner |
| Raw Water Supply | Plant Battery Limits by Owner. |