|  |  |  |
| --- | --- | --- |
| EPC | Weekly Report **19 June 2010** | |
| Date: 19 June 2010 | Project: Sidor Site A, Puerto Ordaz Venezuela | |
| Written By: Patrick Melody | ProEnergy EPC Project Mgr  ProEnergy Site Manager | William Lugo  Patrick Melody |
|  |  |  |

**Table of Contents**

**1. Executive Summary**

**1.1 Safety and Regulatory Compliance**

**1.2 Personnel/Staffing**

**1.3 Weekly Accomplishments**

**1.4 Scheduling Conflicts**

**1.5 Site Manager Commentary and Amplifying Remarks**

**2. Engineering and Design**

**2.1 General Arrangement**

**2.2 Site/Civil/ Structural**

**2.3 Mechanical**

**2.4 Electrical**

**2.5 Instruments & Control**

**2.6 O&M Manuals**

**3. Procurement**

**3.1 Purchase Order Requests**

**3.2 Equipment & Material Quotations**

**3.3 Purchase Order**

**4. Contracts**

**4.1 EPC Contract**

**4.2 Construction Subcontracts**

**4.3 Proposal and Quotes**

**5. Construction**

**5.1 Schedule**

**5.2 Equipment Delivery Status (expediting report)**

**5.3 Civil**

**5.3.1 Site Preparation**

**5.3.2 Centerline Foundation**



**5.3.3 GSU Foundation**

**5.3.4 Auxiliary Foundations**

**5.4.1 Centerline Equipment Installation**

**5.4.2 Centerline Piping Installation**

**5.4.3 Auxiliary Piping Installation**

**5.4.4 Underground Piping Installation**

**5.4.5 Above Ground Piping Installation**

**5.4.6 Balance of Plant (BOP) Piping Installation**

**5.5 Electrical**

**5.5.1 Duct Bank Installation**

**5.5.2 Centerline Electrical Installation**

**5.5.3 Auxiliary Electrical Installation**

**5.5.4 Balance of Plant (BOP) Installation**

**5.6 QA/QC**

**5.6.1 Equipment Testing**

**5.6.2 Nonconformity Report**

**5.6.3 Drawing Revisions**

**5.6.4 CWI Reports**

**5.6.5 As-built Drawings**

**6 Start Up & Commissioning**

**6.1 Schedule**

**6.2 Equipment Status**

**6.3 Punch list**

**6.4 Equipment Checkout**

**6.5 Equipment Functional Test**

**6.6 Equipment Turnover**

**6.7 Performance Testing**

**6.8 Emission Testing**

**7 Mobilization**

**7.1 Schedule**

**7.2 Operating Procedure Development**

**7.3 Operation Staff Training**

**7.4 Spare Parts/Inventory Status**



**1. Executive Summary .**

This report provide an overview of the project activities for the week ending 15 May 2010 for the engineering, procurement, and the construction activities on site.

* 1. **Safety & Regulatory Compliance** 
     + Develop Job Safety Analysis as required.
     + Inspection of motorized equipment prior to usage.
     + Inspection of subcontractor power tools.
  2. **Personnel/Staffing**

|  |  |  |  |
| --- | --- | --- | --- |
| Lugo, Bill | Project Director |  |  |
|  |  |  |  |
| Melody, Patrick | Site Manager | Daniels, Julio | Tool Room (Local) |
| Siros, James | Mech. Supt. | Izquierdo, Weiser | Mat'l. Handler |
| Bird, Jason | Tech. Advisor | Flores, Herman | Tool Room (Local) |
| Horn, Ryan | Tool Room Super. |  |  |
|  |  | Leccia, Karina | Admin Assist |
|  |  | Rojas, Moises | Logistics |
|  |  | Zambrano, Natalia | Translator |
|  |  | Alvarez Josbett | Translator |
|  |  | Jansen Teodoro | Translator |
|  |  |  |  |
|  |  |  |  |
|  |  |  |  |
|  |  |  |  |
|  |  |  |  |

* 1. **Weekly Accomplishments** 
     + GT 100 Install expansion joint
     + GT 100 Install cable tray supports
     + GT 100 Install sprint skid & water injection skid
     + GT 200 Install cable tray supports
     + GT 200 Liquid fuel skid
     + GT 200 Install sprint skid & water injection skid
     + GT 300 Install piping inside the enclosure
     + GT 300 Prep exhaust transition duct
     + GT 300 Exhaust Stack – Interior welding
     + GT 300 – Install GSU transformer
     + GT 300 – Install grating & ladders at filter house
     + GT 300 – Liquid gas fuel module foundation complete
     + GT 300 – Install demister foundation complete
     + GT 300 – Install water wash foundation complete
     + Complete Duct bank – MH 1 to GT 300
     + Complete Duct bank – MH 8 to GT 200
     + Complete Duct bank – MH 9 to gas compressor
     + Utility Bldg. Install anchor bolts for PEB
     + Water Treatment Bldg – Install floor drain
     + POB - Install black start generator
     + BOP - Excavate storm drain on west side of GT300
     + BOP – Demin water tank mud mat
     + BOP – RO Tank foundation complete
     + BOP - Switch Yard foundations ongoing
     + BOP - Switch yard precast manholes complete
     + BOP – Install fire line
     + BOP - Install process pipe
     + BOP – Oily water separator foundation in process
     + BOP – Fire line Hydro Test East side



**1.4– Scheduling Conflicts**

* ***CPM schedule was issued 14 June 2010.*** Impacts resulting from lack of progress payments is being reviewed for inclusion
  1. **– Site Managers Commentary and Amplifying Remarks**
* Civil Contractor has reduced manpower this week due to the payment issue. No Saturday work is planned after 12 June 10. GT 300 duct bank 7 foundations, switch yard and water treatment building will be adversely affected.
* ***Power line which was restraining excavation of tank foundations was removed on 18 June 2010. Excavation to begin on Monday, 21 June 2010***
* GT 300 GSU transformer was damaged in shipment***. Repair will be made in field by heat straightening damaged tube.***
* 7EA Dual fuel conversion is scheduled to start on 21 June 10 provided commercial issues are resolved. Approximately 6 week duration. **Pending receipt of payment.**
* The following components have been sent to Termozulia. Beckwith; Electro Industries volt/amp meter; coupling bolts; purge and vent valves for fuel gas module; and ignition transformer. Lead times are critical for replacement of these items. ***Control cards for 7EA are also required this week by Termozulia***

**2 Engineering and Design**

**2.1 – General Arrangement-**

**2.2 – Site /Civil /Structural**

**2.3 – Mechanical**

**2.4 – Electrical**

* + - Additional detail is required to stub up conduit at the location required. A list of foundation has been provided to the engineer for his action.
    - Grounding grid drawings are required.

**2.5 – Instrumentation**

* **Ongoing**

**2.6 – O&M Manuals –**

* **Ongoing**

**3 Procurement**

**3.1 – Purchase Order Requests**

* A local vendor list is being developed with the assistance of SIDOR.
* The lack of Progress Payments is restricting issuing PO’s to local subcontractors and vendors.

1. **– Equipment & Material Quotations**

* Local procurement is hampered by financial restraints

**3.3 - Purchase Order –**

**4 Contracts**

**4.1 – EPC Contract –**

**4.2 – Construction Subcontracts –**

**4.3 – Proposal & Quotes**

**5 Construction**

* **5.1 Schedule**

Impacts resulting from lack of progress payments is being reviewed for inclusion

* CPM schedule was issued 14 June 2010.

**5.2 Equipment Delivery**

**5.3 Mechanical**

* GT 100 – GT Erection is complete
* GT 200 – GT Erection is complete. Awaiting arrival of turbine for installation.
* GT 300 – GT Erection is complete

**5.4 Electrical**

* Installation of Manholes and duct banks is ongoing.
* On site meeting was held to resolve high voltage and switchyard final design.

**5.5 QA/QC –**

* Inspections of concrete placement, excavation, and backfill activities is ongoing.

**6 Startup & Commissioning**

* Pending.

**7 Startup Mobilization**



GT 300 7EA GSU Transformer



Duct Bank MH1 to GT 300 PEECC