| EPC | Weekly Report 26 June 2010 |  |
| --- | --- | --- |
| Date: 26 June 2010 | Project: Sidor Site A, Puerto Ordaz Venezuela |  |
| Written By: Patrick Melody | ProEnergy EPC Project Mgr ProEnergy Site Manager | William Lugo Patrick Melody |

Table of Contents

1. Executive Summary

1.1 Safety and Regulatory Compliance

1.2 Personnel/Staffing

1.3 Weekly Accomplishments

1.4 Scheduling Conflicts

1.5 Site Manager Commentary and Amplifying Remarks

2. Engineering and Design

2.1 General Arrangement

2.2 Site/Civil/ Structural

2.3 Mechanical

2.4 Electrical

2.5 Instruments & Control

2.6 O&M Manuals

3. Procurement

3.1 Purchase Order Requests

3.2 Equipment & Material Quotations

3.3 Purchase Order

4. Contracts

4.1 EPC Contract

4.2 Construction Subcontracts

4.3 Proposal and Quotes

5. Construction

5.1 Schedule

5.2 Equipment Delivery Status (expediting report)

5.3 Civil

5.3.1 Site Preparation

5.3.2 Centerline Foundation

5.3.3 GSU Foundation

5.3.4 Auxiliary Foundations

5.4.1 Centerline Equipment Installation

5.4.2 Centerline Piping Installation

5.4.3 Auxiliary Piping Installation

5.4.4 Underground Piping Installation

5.4.5 Above Ground Piping Installation

5.4.6 Balance of Plant (BOP) Piping Installation

5.5 Electrical

5.5.1 Duct Bank Installation

5.5.2 Centerline Electrical Installation

5.5.3 Auxiliary Electrical Installation

5.5.4 Balance of Plant (BOP) Installation

5.6 QA/QC

5.6.1 Equipment Testing

5.6.2 Nonconformity Report

5.6.3 Drawing Revisions

5.6.4 CWI Reports

5.6.5 As-built Drawings

6 Start Up & Commissioning

6.1 Schedule

6.2 Equipment Status

6.3 Punch list

6.4 Equipment Checkout

6.5 Equipment Functional Test

6.6 Equipment Turnover

6.7 Performance Testing

6.8 Emission Testing

7 Mobilization

7.1 Schedule

7.2 Operating Procedure Development

7.3 Operation Staff Training

7.4 Spare Parts/Inventory Status

1. Executive Summary .

This report provide an overview of the project activities for the week ending 15 May 2010 for the engineering, procurement, and the construction activities on site.

  - Safety & Regulatory Compliance

    - Develop Job Safety Analysis as required.

    - Inspection of motorized equipment prior to usage.

    - Inspection of subcontractor power tools.

  - Personnel/Staffing

| Lugo, Bill | Project Director |  |  |
| --- | --- | --- | --- |
| Melody, Patrick | Site Manager | Daniels, Julio | Tool Room (Local) |
| Siros, James | Mech. Supt. | Izquierdo, Weiser | Mat'l. Handler |
| Bird, Jason | Tech. Advisor | Flores, Herman | Tool Room (Local) |
|  |  | Leccia, Karina | Admin Assist |
|  |  | Rojas, Moises | Logistics |
|  |  | Zambrano, Natalia | Translator |
|  |  | Alvarez, Josbett | Translator |
|  |  | Jansen Teodoro | Translator |

  - Weekly Accomplishments

    - GT 100 Install expansion joint complete

    - GT 100 Install line breaker switch

    - GT 200 Install cable tray supports

    - GT 200 Install line breaker switch

    - GT 200 Erect H frame for turbine installation

    - GT 300 Install piping inside enclosure

    - GT 300 Exhaust Stack – Interior welding

    - GT 300 Install exhaust stack transition joint

    - GT 300 Install drain piping

    - GT 300 Excavate for Auxiliary transformer

    - GT 300 Excavate for generator breaker foundation

    - GT 300 Excavate for water injection skid

    - Duct bank – MH 1 to PECC

    - BOP - Install storm drain pipe and structures on west side of GT300

    - BOP – Demin water tank install forms and rebar

    - BOB -  Install auxiliary transformer TA2

    - BOP – Raw water tank – Excavation complete

    - BOP – Fuel Storage tanks – Excavation complete, engineered backfill placement

    - BOP - Switch Yard foundations ongoing

    - BOP – Install fire line

    - BOP -  Install process pipe

    - BOP – Oily water separator foundation complete

    - BOP – Fire line Hydro Test East side

    - BOP – Erect Utility Bldg.

    - BOP Utility Bldg – Install MCC crates on slab

1.4– Scheduling Conflicts

- CPM schedule was issued 14 June 2010.  Impacts resulting from lack of progress payments is being reviewed for inclusion

  - – Site Managers Commentary and Amplifying Remarks

- Civil Contractor continues to work with reduced manpower due to payment issues. No Saturday work is scheduled.  GT 300 duct bank 7 foundations, switch yard and water treatment building will be adversely affected.

- Power line which was restraining excavation of tank foundations was removed on 18 June 2010. Excavation of tanks is complete. Placement of engineered backfill in process.

- GT 300 GSU transformer was damaged in shipment. Repair will be made in field by heat straightening damaged tube with oversight by high voltage installation team

- 7EA Dual fuel conversion is scheduled to start on 21 June 10 provided commercial issues are resolved. Approximately 6 week duration. Pending receipt of payment.

- The following components have been sent to Termozulia. Beckwith; Electro Industries volt/amp meter; coupling bolts; purge and vent valves for fuel gas module; and ignition transformer. Lead times are critical for replacement of these items. Control cards for 7EA are also required this week by Termozulia.

2 Engineering and Design

2.1 – General Arrangement-

2.2 – Site /Civil /Structural

2.3 – Mechanical

2.4 – Electrical

    - Additional detail is required to stub up conduit at the location required. A list of foundation has been provided to the engineer for his action.

2.5 – Instrumentation

- Ongoing

2.6 – O&M Manuals –

- Ongoing

3 Procurement

3.1 – Purchase Order Requests

- A local vendor list is being developed with the assistance of SIDOR.

- The lack of Progress Payments is restricting issuing PO’s to local subcontractors and vendors.

- Numerous PO have been prepared for execution when progress payment has been received.

3.2– Equipment & Material Quotations

3.3 - Purchase Order –

4 Contracts

4.1 – EPC Contract –

4.2 – Construction Subcontracts –

4.3 – Proposal & Quotes

- Proposal for erection of tanks and Pre Engineered Buildings have been received and are being evaluated.

5 Construction

- 5.1  Schedule

Impacts resulting from lack of progress payments is being reviewed for inclusion

- CPM schedule was issued 14 June 2010.

5.2  Equipment Delivery

5.3  Mechanical

- GT 100 – GT Erection is complete

- GT 200 – GT Erection is complete. Awaiting arrival of turbine for installation.

- GT 300 – GT Erection is complete

5.4  Electrical

- Installation of Manholes and duct banks is ongoing.

5.5 QA/QC –

- Inspections of concrete placement, excavation, and backfill activities is ongoing.

6 Startup & Commissioning

- Pending.

7 Startup Mobilization

Demin Water Tanks Forms/Rebar & Excavation Raw Water Tank

Utility Bldg. Erection