CVG SIDOR POWER PROJECT SITE “A”

DATE:  28 September 2010, Tuesday

PROJECT #: 410-3202

LOCATION: SIDOR Industrial Area, Puerto Ordaz, Venezuela

SITE MANAGER: Patrick Melody

TEMPERATURE:  88 F

RANGE: 85 to 95 F

SITE CONDITIONS:  Partly Sunny

/

PERSONNEL ON SITE:

| Lugo, Bill | Project Director | Newan, Miguel | Mat'l. Handler Local |
| --- | --- | --- | --- |
| Melody, Patrick | Site Manager | Izquierdo, Weiser | Mat'l. Handler Local |
| Siros, James | Mechanical Supt. | Herman, Flores | Tool Room Local |
| Riley, Jasper | Elect. Supt. | Monasterios, O | Safety Local |
| McCormick, William | Safety Manager | Leccia, Karina | Admin. Local |
| Frawely, Ted | Elect. Supt. | Zambrano Natalia | Elect. Eng. Local |
| Lynch, Patrick | Piping Supt. | Alvarez, Josbett | Admin. |
| Siros, Melinda | Turn Over | Lugo, Lee | Translator |
| Montgomery, Mike | QA/QC | Rojas, Moises | Procurement Local |
| Maxey, Daniel | 7EA Technical Assist. | Pollack, Mike | Manager Aero Dir. |
| Boykin, Ken | Start Up Manager | Medina, David | High Voltage |
| Bingham, Allen | Start Up | Villareal, Luis | High Voltage |
| Graves, Mike | Start Up | Selenia, Jimenez | High Voltage |
| Hicks, Todd | Start Up | Smoak, Eric | High Voltage |
| Flowers, Caleb | I & C | Sprague, Randy | High Voltage |
|  |  | Flowers, Kurt | I & C |
|  |  | Doran, Patrick | I & C |

SUBCONTRACTOR PERSONNEL:

CIVIL

Operators                              6                             Carpenter                             10                           Electrician                              2                            Concrete Finisher                   9                                                            Laborers                               25                            Iron Workers                          4

Truck Driver                           3                             Welders                                 3                              Plumber                                 2         		  Surveyor                                3

Oilers                                     2                             Mechanic Heavy                    2

Total  60

Mechanical

Welders                                  9                           Fitters/Mechaics                   16

Helpers                                 18                           Operators                               2

Electrical

Electricians                           30                           Helpers                                 10

Instrumentation

Instrument Techs		  10

- GENERAL ITEMS

    - Design and procurement for the project needs to be completed as soon as possible to support current project schedule. Daily meetings are held with the design team and/or field engineers to follow up on the design and to discuss design changes

- Cathodic design for piping system needs to be finalized. Meeting was held on site with local subcontractor. It was agreed to proceed on EPC basis.  Cost proposal has been received from subcontractor. Design has been received. Installation in process.

- DCS Equipment will be shipped 14 Sept 2010 from Sedalia.

- GT 100 & 200 MCC is not correctly configured. Bus bar is undersized. Capacity not adequate for all required equipment. Report has been released. Material is being sourced. Furthermore, internal wiring of the buckets does not match the design drawings. Rewiring of the motor starters is in process. This activity is adding a lot of additional load to the construction and start up crew as well as an impact on the schedule. Additional materials are being purchased to resolve the situation. Rewiring of MCC 200 is complete

- Materials and equipment delivery delays are having a substantial impact on the construction and star-up schedule and associated activities. Equipment and Materials such as power and control cable (ETAs 23 Sept 2010) 40 - 45% of the cable; LM 6000. Material from the Industrial Cape which arrived in Guanta is experiencing delays in over land shipping. The National Guard is unable to commit resources for convoy escort duties due to the National Election on Sunday. Expect delivery will be delayed until Wednesday.

- CLIENT ISSUES/CONCERNS:

    - Preliminary discussions were held with SIDOR to discuss gas blows and alternative options. To the extent possible, SIDOR would like to minimize the need for gas blows. SIDOR has agreed to gas blows and has requested a written procedure for gas blows along with a site plan indicating location of gas blow offs.  A format has been reviewed. Written procedure is in process by Start Up Group.

    - Sidor has indicated that the water supply is out of specification and will require pretreatment. SIDOR’s water treatment consultant has furnished a recommendation which is being reviewed by EDG. EDG has met with the SIDOR’s vendor to discuss their recommendations. EDGI just advised that additional equipment will be needed to be able to treat the water based on the new sample analysis provided by SIDOR. A contract change order is in process.

- Derwick has verbally indicated that the Fuel storage tank, fuel unloading bldg. and related utilities will be removed from our scope of work. An email has been received from Derwick deleting certain elements of the fuel storage systems. Prior to project closeout it will be necessary to complete the LM 6000 dual fuel conversion. Procurement/delivery of equipment and materials is pending.

- CIVIL:

    - BOP - Site grading/Install Yard Stone

    - BOP – Erect Control Bldg.

- CONCRETE FOUNDATIONS:

    - Foundations Complete

- MECHANICAL:

    - GT 200 – Weld liner plate in stack

    - GT 200 – Install Drain Piping from Filter House

    - GT 200 – Prep for generator flush

    - GT 200 – Oil Flush Ongoing

    - GT 300 Install fogging system

    - GT 300 Complete Mechanical Punch List

    - BOP – Install Raw Water Tank Pipe connection

    - BOP – Install Cooling Water Piping

    - BOP -  Utility Bldg. Install Water Injection Piping

    - BOP – Install Piping in Water Treatment Building

    - BOP – Pre alignment of gas compressors for LM 6000

    - Demin Water Tanks – Passavate Welds

    - Raw Water Tanks – Sandblast roof

- ELECTRICAL:

    - GT 100 – Terminate 15 kv cable in SWBD 100

    - GT 200 – Install cable MTTB to Filter House

    - GT 100 & GT 200 Rewire MCC’s per design drawings

    - GT 300 Install Conduit and Cable tray

    - High Voltage – Tension Cables

    - BOP –  Utility Bldg. Terminate Cables at UPS

    - BOP – Test Leads and Windings on the Black Start Generator

    - BOP – Locked out all Equipment in theMCC’s

    - BOP – Commission and Test Black Start Generator

    - BOP – Water Treatment Install Conduit to Air Compressor

    - BOP – Energize Battery Chargers

    - BOP - Install ground grid

    - BOP – Install MCC’s in Water Treatment

    - BOP – Gas Compressor Bldg. Terminations Ongoing

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS:

    - General

      - CPS Schedule updates on going.

    - Contract Milestone Payments

      - Completed Milestone Payments (50%)

Complete

      - Gas Turbines on Foundation (10%)

Complete

8.1.2.3     Civil Foundations Complete (25%)

Complete

8.1.2.4      Electrical/Mechanical Complete (10%)

October 31, 2010

      - Start- up Complete and Ready to Export Power (5%)

November 9, 2010

Note (*):  These dates are being revised based upon an accelerated schedule.

    - Target Ready for Start-Up Dates

      - Unit 100 – LM6000

October 10, 2010 *

      - Unit 200 – LM6000

October 10, 2010 *

      - Unit 300 – 7EA

October 31, 2010

Note (*): These dates have been revised due to the late delivery of material. Including cables, ESD valves, MCC’s that were not fabricated correctly, and missing instrumentation.

A revised Start up Schedule has been received with a 145 day duration. Durations will be evaluated prior to incorporation into the schedule.

- CRITICAL AREAS OF CONCERN:

- Design and procurement activities for the project need to be completed as soon as possible to support current project schedule. We continue to have daily communications with the design team in Tulsa as well as the field engineers on the design progress.

- EDG has completed the Cable Schedule for the project. We currently have 50% of the cable required on site. Other PES sites, CVG B, and SIDOR have been providing cable as available. Cable procurement is ongoing. Schedule is being severely impacted due to lack of cable on site.

    - SAFETY:

        - Develop JSA as needed

        - Inspection of subcontractor power tools.

        - Inspection of motorized equipment prior to usage.

        - Scaffold and trenching inspections ongoing.

        - Site Orientation for New Staff

        - Site Meeting to initiate lock out tag out

    - OUTSTANDING DRAWINGS:

    - DRAWINGS ISSUED:

- PICTURES:

Gas Compressor Prep for Grout Placement

Switch Yard Cable Installation