|  |
| --- |
| **CVG SIDOR POWER PROJECT SITE “A”** |
|  |

**DATE: 4 October 2010, Sunday**

**PROJECT #: 410-3202**

**LOCATION: SIDOR Industrial Area, Puerto Ordaz, Venezuela**

**SITE MANAGER: Patrick Melody**

**TEMPERATURE: 88 F**

**RANGE: 85 to 95 F**

**SITE CONDITIONS: Partly Sunny/Rain over night**

**/**

**PERSONNEL ON SITE:**

|  |  |  |  |
| --- | --- | --- | --- |
| Lugo, Bill | Project Director | Newan, Miguel | Mat'l. Handler Local |
| Melody, Patrick | Site Manager | Izquierdo, Weiser | Mat'l. Handler Local |
| Siros, James | Mechanical Supt. | Herman, Flores | Tool Room Local |
| Riley, Jasper | Elect. Supt. | Monasterios, O | Safety Local |
| McCormick, William | Safety Manager | Leccia, Karina | Admin. Local |
| Frawely, Ted | Elect. Supt. | Zambrano Natalia | Elect. Eng. Local |
| Lynch, Patrick | Piping Supt. | Alvarez, Josbett | Admin. |
| Siros, Melinda | Turn Over | Lugo, Lee | Translator |
| Montgomery, Mike | QA/QC | Rojas, Moises | Procurement Local |
| Maxey, Daniel | 7EA Technical Assist. | Pollack, Mike | Manager Aero Dir. |
| Boykin, Ken | Start Up Manager | Medina, David | High Voltage |
| Bingham, Allen | Start Up | Villareal, Luis | High Voltage |
| Graves, Mike | Start Up | Selenia, Jimenez | High Voltage |
| Hicks, Todd | Start Up | Smoak, Eric | High Voltage |
| Flowers, Caleb | I & C | Sprague, Randy | High Voltage |
|  |  | Flowers, Kurt | I & C |
|  |  | Doran, Patrick | I & C |

**SUBCONTRACTOR PERSONNEL:**

**CIVIL**

Operators 6 Carpenter 10 Electrician 2 Concrete Finisher 9 Laborers 25 Iron Workers 4

Truck Driver 3 Welders 3 Plumber 2 Surveyor 3

Oilers 2 Mechanic Heavy 2

**Total 60**

**Mechanical**

Welders 9 Fitters/Mechaics 16

Helpers 18 Operators 2

**Electrical**

Electricians 30 Helpers 10

**Instrumentation**

Instrument Techs 10

1. **GENERAL ITEMS**
   * 1. Design issues and procurement for the project needs to be completed as soon as possible to support current project schedule. Daily meetings are held with the design team and/or field engineers to follow up on the design and to discuss design changes and or issues.

* Cathodic design for piping system has been finalized. Estimated completion date 15 October 2010.
* DCS Equipment ***was shipped 27 Sept 2010 from Sedalia. ETA Guanta 8 October 2010. ETA Site 12 October 2010.***
* GT 100 & 200 MCC is not correctly configured. Bus bar is undersized. Capacity not adequate for all required equipment. Report has been released***.*** Material is being sourced. Furthermore, internal wiring of the buckets does not match the design drawings. Rewiring of the motor starters is in process.This activity is adding a lot of additional load to the construction and start up crew as well as an impact on the schedule. Additional materials are being purchased to resolve the situation. Rewiring of MCC 200 is complete. Rewiring of MCC 100 is ongoing.
* Materials and equipment delivery delays are having a substantial impact on the construction and star-up schedule and associated activities. Equipment and Materials such as power and control cable. Anticipated cable delivery ETA Site 4 Oct 2010 with balance to follow 11 October 2010. ***Delivery from the Industrial Dolphin is expected on Saturday, 2 October 2010.***

1. **CLIENT ISSUES/CONCERNS:**

* Preliminary discussions were held with SIDOR to discuss gas blows and alternative options. To the extent possible, SIDOR would like to minimize the need for gas blows***.*** SIDOR has agreed to gas blows and has requested a written procedure for gas blows along with a site plan indicating location of gas blow offs. A format has been reviewed. Written procedure is in process by Start Up Group.
* Sidor has indicated that the water supply is out of specification and will require pretreatment. SIDOR’s water treatment consultant has furnished a recommendation which is being reviewed by EDG. EDG has met with the SIDOR’s vendor to discuss their recommendations. EDGI just advised that additional equipment will be needed to be able to treat the water based on the new sample analysis provided by SIDOR. A contract change order has been submitted to Derwick. Awaiting formal approval.
* Derwick has verbally indicated that the Fuel storage tank, fuel unloading bldg. and related utilities will be removed from our scope of work. An email has been received from Derwick deleting certain elements of the fuel storage systems. Prior to project closeout it will be necessary to complete the LM 6000 dual fuel conversion. Procurement/delivery of equipment and materials is pending.

1. **CIVIL:**
   * 1. BOP - Site grading/Install Yard Stone
     2. BOP – Erect Control Bldg.
     3. BOP - Grouting Gas Compressors
     4. BOP - Concrete placement for bollards
2. **CONCRETE FOUNDATIONS:**
   * 1. Foundations Complete
3. **MECHANICAL:**
   * 1. GT 200 – Install on turbine exhaust
     2. GT 300 – Install Liquid Fuel piping
     3. GT 300 – Install Instrument Air Piping
     4. BOP – Install Cooling Water Piping
     5. BOP - Utility Bldg. Install Water Injection Piping
     6. BOP – Install Piping in Water Treatment Building
     7. Raw Water Tanks – Sandblast walls
4. **ELECTRICAL:**
   * 1. GT 100 Rewire MCC’s per design drawings
     2. GT 100 Cable Installation
     3. GT 300 - Install Conduit and Cable tray
     4. BOP – Inspecting Water Treatment & Gas Compressor MCC for compliance with design documents
     5. BOP - Install ground grid
5. **INSTRUMENTATION AND CONTROLS:**
6. **SCHEDULED ITEMS:** 
   * 1. ***General***
        1. CPS Schedule updates on going.
     2. ***Contract Milestone Payments***
        1. Completed Milestone Payments (50%)

Complete

* + - 1. Gas Turbines on Foundation (10%)

Complete

***8.1.2.3*** Civil Foundations Complete (25%)

Complete

***8.1.2.4*** Electrical/Mechanical Complete (10%)

October 31, 2010

* + - 1. Start- up Complete and Ready to Export Power (5%)

November 30, 2010

***Note (\*): These dates are being revised based upon an accelerated schedule.***

* + 1. ***Target Ready for Start-Up Dates***
       1. ***Unit 100 – LM6000***

***October 15, 2010 \****

* + - 1. ***Unit 200 – LM6000***

***October 15, 2010 \****

* + - 1. ***Unit 300 – 7EA***

October 31, 2010

Note (\*): These dates have been revised due to the late delivery of material. Including cables, ESD valves, MCC’s that were not fabricated correctly, and missing instrumentation.

A revised Start up Schedule has been received with a145 day duration. Durations will be evaluated prior to incorporation into the schedule.

1. **CRITICAL AREAS OF CONCERN:**

* Design and procurement activities for the project need to be completed as soon as possible to support current project schedule. We continue to have daily communications with the design team in Tulsa as well as the field engineers on the design progress.
* EDG has completed the Cable Schedule for the project. We currently have 50% of the cable required on site. Other PES sites, CVG B, and SIDOR have been providing cable as available. Cable procurement is ongoing. Schedule is being severely impacted due to lack of cable on site.
* GT 200 – Generator Lube Oil Pump shaft seal has failed. Sedalia sourcing replacement parts from Tuttle.
  1. **SAFETY:**
     + - 1. Develop JSA as needed
         2. Inspection of subcontractor power tools.
         3. Inspection of motorized equipment prior to usage.
         4. Scaffold and trenching inspections ongoing.
         5. Site Orientation for New Staff
  2. **OUTSTANDING DRAWINGS:**
  3. **DRAWINGS ISSUED:**

1. **PICTURES:**

****

**Raw Water Tank Coating In Progress**