## PL CVG A
Construction Activities - Punch List
Power Station - CVG A
Item | PO | Activity Description | Priority | Priority | Responsible Contractor | Start Date | Completion Date | Orig Competion | Estimated Completion | % Completion | Notes/Comments
1 | LTR | Purchase and installation of acustic walls for 7EA |  |  |  | 2010-10-25 |  |  | 2010-10-30 | 0% | Awaiting quotes from vendors.
2 | 656 | Fabrication and installation of shed for water forwarding pumps (400A/B & 5000A/B/C) |  | 1 | TDA | 2010-10-06 |  |  | 2010-10-19 | 95% | Shed was fabricated and will be installed on Wednesday Oct 14, 2010
3 | 540 | Sand blasting and painting of raw water tank | 20 | 1 | TDA | 2010-09-24 |  |  | 2010-10-20 | 85% | Ongoing. Exterior blasting and primer complete. Interior ongoing.
4 | 604 | Installation of bridge cranes - Admin/control building | 24 | 1 | TDA | 2010-10-11 |  |  | 2010-10-30 | 0% | We have the quote/ preparing PO. On hold because of design issues
5 | 589 | Fabrication of stair, platforms and access to various pieces of equipment | 30 | 1 | TDA | 2010-10-11 |  |  | 2010-10-22 | 60% | All fabrication will be provided by the supplier between 20 Oct to 23 Oct.
6 | 589 | Guard rails and walk away for step up transformers (GSUs) | 37 | 1 | TDA | 2010-10-11 |  |  | 2010-10-20 | 20% | Fabrication ongoing.
7 | 641 | Complete modification of changes in gas compressor electrical room -- URGENT--- EDGI design required | 1 | 1.5 | Movensa | 2010-10-05 |  |  | 2010-10-20 | 50% | Ongoing based on EDGI recommendation
8 | 428 | Supply and installation of all walls and electrical system - Admin & control building office area | 22 | 1.5 | Movensa | 2010-10-11 |  |  | 2010-10-29 | 0% | Movensa to mobilize 20 October
9 | 428 | Supply and instalation of electrical system including light fixtures and receptacles for the admin/control building - Office area only | 28 | 1.5 | Movensa | 2010-10-11 |  |  | 2010-10-29 | 0% | Movensa to start as soon as the building is ready for them to move in
10 | 638 | Supply and installation of gas compressor bldg electrical room double door | 21 | 1.8 | Corpometal | 2010-09-29 | 2010-10-10 |  | 2010-10-10 | 100% | Complete
11 | 709 | Maintenance of existing air condition units associated with the aux equipment for 7EA |  | 2 | Refrivialca | 2010-10-11 |  |  | 2010-10-20 | 0% | Ongoing. Need power to the unit
12 | 713 | HVAC electrical/control equipment room for the gas compressor bldg |  | 2 | Refrivialca |  |  |  | 2010-10-20 | 0% | This is scheduled to start on Oct 14, 2010
13 | 712 | HVAC electrical/control equipment room for the water treatment building |  | 2 | Refrivialca |  |  |  | 2010-10-20 | 0% | This is scheduled to start on Oct 14, 2010
14 | 572 | Supply and installation of HVAC for admin/control Bldg including air conditioning ducts & HVAC equipment | 23 | 2 | Refrivialca | 2010-10-11 |  |  | 2010-10-30 | 20% | On going. Need to follow up with the supplier until is complete.
15 |  | Labeling & marking of Mechanical /Elect Equipment | 45 | 3 | Table Sur |  |  |  | 2010-10-30 | 0%
16 | 640 | Purchase and installation of termination box for 7EA gen breaker |  | 3 | Tablesur | 2010-10-06 | 2010-10-10 |  | 2010-10-12 | 100% | Complete
17 | 640 | Purchase and installation of 13.8kV roof panels |  | 3 | Tablesur | 2010-10-06 |  |  | 2010-10-20 | 0% | Ongoing. Unit 200 is completed. Unit 100 is scheduled to be supplied by Oct 14, 2010
18 | 549 | Installation of deluge system - Step up transformer 100, 200 & 300 | 18 | 5 | Renain CA | 2010-09-29 |  |  | 2010-10-28 | 30% | Ongoing
19 | 584 | Complete painting of pipes | 43 | 5 | Repaint | 2010-09-28 |  |  | 2010-10-30 | 30% | Ongoing
20 | 552 | Complete painting of other facilities, structures, and others | 32 | 5 | Repaint | 2010-09-27 |  |  | 2010-10-30 | 60% | Ongoing
21 | 622 | Supply and Installation of Guardrails - Oily water separator | 19 | 6 | ISI | 2010-09-27 | 2010-10-04 |  | 2010-10-04 | 100% | Complete
22 |  | Mechanical completion - Mechanical Activities | 42 | 6 | ISI | 2010-07-01 |  |  | 2010-10-30 | 30% | Ongoing .See attached punch list
23 | 569 | Electrical completion - Electrical Activities | 44 | 6 | Sialca | 2010-07-01 |  |  | 2010-10-31 | 30%
24 | 569 | Installation of outdoor lighting including lighting poles and light fixtures. | 13 | 7 | Sialca | 2010-10-11 |  |  | 2010-10-25 | 20%
25 | 569 | Complete ground grid - 115kV Switchyard including connection to the existing 115kV switchyard ground grid (through existing road) | 14 | 7 | Sialca | 2010-09-06 |  |  | 2010-10-24 | 98%
26 | 569 | Complete ground grid - Other areas | 15 | 7 | Sialca | 2010-09-06 |  |  | 2010-10-22 | 95%
27 | 569 | Complete grounding of new fence around the 115 kV switchyard | 16 | 7 | Sialca | 2010-10-04 |  |  | 2010-10-20 | 40% | Ongoing
28 | 569 | Complete Grounding - all Equipment, Skids & Structures | 17 | 7 | Sialca | 2010-09-06 |  |  | 2010-10-25 | 50%
29 | 569 | Supply and installation of electrical system including light fixtures and receptacles for the water treatment building (30-001, Sheet 2) | 25 | 7 | Sialca | 2010-10-11 |  |  | 2010-10-28 | 0% | Issued PO for lighting fixtures. Waiting for down payment.
30 | 569 | Supply and installation of electrical system including light fixtures and receptacles for the utility building (30-003, Sheet 2) | 26 | 7 | Sialca | 2010-10-11 |  |  | 2010-10-28 | 0% | Issued PO for lighting fixtures. Waiting for down payment.
31 | 569 | Supply and installation of electrical system including light fixtures and receptacles for the gas compressor building | 27 | 7 | Sialca | 2010-10-11 |  |  | 2010-10-28 | 0% | Issued PO for lighting fixtures. Waiting for down payment.
32 | 569 | Supply and installation of electrical system including light fixtures and receptacles for the admin/control building - Warehouse area. | 29 | 7 | Sialca | 2010-10-11 |  |  | 2010-10-28 | 0% | Issued PO for lighting fixtures. Waiting for down payment.
33 | 569 | Installation Control Equip - PLC / Remote IO Cabinet in Water treatment Bldg | 33 | 7 | Sialca | 2010-10-12 |  |  | 2010-10-22 | 30% | Equipment received. Installation ongoing
34 | 569 | Installation Control Equip - PLC / Remote IO Cabinet in Compressor Bldg | 34 | 7 | Sialca | 2010-10-12 |  |  | 2010-10-22 | 30% | Equipment received. Installation ongoing
35 | 569 | Installation Control Equip - PLC / Remote IO Cabinet in Utility Bldg | 35 | 7 | Sialca | 2010-10-12 |  |  | 2010-10-22 | 30% | Equipment received. Installation ongoing
36 | 569 | Installation Control Equip - PLC / Remote IO Cabinet in PDC Bldg | 36 | 7 | Sialca | 2010-10-12 |  |  | 2010-10-22 | 30% | Equipment received. Installation ongoing
37 | 569 | Installation Control Equipment & Cabinets in Control/Admin. Bldg | 38 | 7 | Sialca | 2010-10-12 |  |  | 2010-10-26 | 0% | Equipment received. Waiting on the completion of the building to install equipment
38 | 518 | Supply and installation of cathodic protection for the piping | 9 | 8 | Saeli CA | 2010-09-28 |  |  | 2010-10-20 | 85% | Ongoing
39 | 441 | Supply and install drainage pipe - North area of CVG Site A ( Drg # 10-003 / Sheet 6) | 2 | 9 | Consorcio Megavatio |  |  |  | 2010-10-26 | 0%
40 | 441 | Complete site grading - North area of CVG Site A | 3 | 9 | Consorcio Megavatio | 2010-09-01 |  |  | 2010-10-26 | 75%
41 | 441 | Complete South- North road including asphalt | 4 | 9 | Consorcio Megavatio | 2010-09-01 | 2010-09-30 |  | 2010-09-30 | 100% | Complete
42 | 441 | Complete site grading - Other areas | 5 | 9 | Consorcio Megavatio | 2010-09-01 |  |  | 2010-10-25 | 80%
43 | 590 | Complete Grouting - Unit 200 | 6 | 9 | Consorcio Megavatio | 2010-09-21 | 2010-09-23 |  | 2010-09-23 | 100% | Complete
44 | 590 | Complete Grouting - Unit 300 | 7 | 9 | Consorcio Megavatio | 2010-10-11 |  |  | 2010-10-15 | 0% | Ongoing
45 | 590 | Complete Grouting - Unit 100 | 8 | 9 | Consorcio Megavatio | 2010-10-06 | 2010-10-10 |  | 2010-10-15 | 100% | Complete
46 | 590 | Complete Grouting - 115kV Switchyard Equipment & Structures | 10 | 9 | Consorcio Megavatio | 2010-09-20 | 2010-09-29 |  | 2010-10-08 | 100% | Complete
47 | 590 | Complete Grouting - all Equipment, Skids & Structures | 11 | 9 | Consorcio Megavatio | 2010-09-23 |  |  | 2010-09-26 | 45% | Ongoing
48 | 441 | Complete foundation for light poles | 12 | 9 | Consorcio Megavatio | 2010-10-12 |  |  | 2010-10-27 | 50% | Ongoing
49 | 441 | Complete work associated with the sewer for the adm/ control Building ( water) | 31 | 9 | Consorcio Megavatio | 2010-08-15 | 2010-08-30 |  | 2010-09-29 | 100% | Complete
50 | 441 | Underground conduits for demin and raw water tanks, see drawings 60-103 & 60-104 | 39 | 9 | Consorcio Megavatio | 2010-08-15 | 2010-08-30 |  | 2010-09-29 | 100% | Complete
51 | 441 | Civil completion - Civil Activities | 41 | 9 | Consorcio Megavatio | 2010-07-01 |  |  | 2010-10-25 | 90% | Ongoing
52 | 441 | Complete Generator removal Slab | 40 | 9 | Consorcio Megavatio |  |  |  | 2010-10-30 | 0%
53 | 711 | Gas Compressor Inspection / Maintenance | 40 | 9 | Fluix de Venezuela | 2010-10-19 |  |  | 2010-11-30 | 0% | To start working on gas compressors on 19 Oct 2010
54 | LTR | 115kV Bus Bar Modification to Align it with the Existing 115kV switchyard |  |  | LATER | 2010-10-10 |  |  | 2010-11-30 | 20% | Working on design modification
55
Notes
1. Critical Activities
2. Activities Completed