# CVG SIDOR POWER PROJECT SITE “B”

# DATE:4 August, 2010, Tuesday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  85 F

RANGE: 76 to 88

SITE CONDITIONS: Rainy all day

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Unfilled Mechanical/Piping (local ASAP)

Mark Hanks - Electrical Supt

Jose Garcia - Elect. Field Eng. (local)

Kyle Roskam - Civil Supt

Felix Martinez-QA/QC

Jason Bird - 7EA TA (A&B)

Melinda Siros – Document Control/Turn Over Coordinator (A&B)

MATERIAL SUPPORT:

José Angel Gonzales – Material (Local)

Paul Olivo – Materials

Jose	– tool room (Local)

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila García – Translator/Doc Control (Local)

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio

General Superintendant		1

Safety					1

Foremen				3

Electricians				0

Operators				0                      Surveyor				1

Carpenters				7

Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				4

Truck Drivers				0

Concrete Finishers			0

Oilers					0

Plumbers				0

Iron Workers				10

Helpers				4

Welders				2

Total:					35

SUBCONTRACTOR PERSONNEL: ISI

General Superintendant		0

Safety					1

Foremen				1

Operators				1

Oiler Helper				0

Welders				5

Crane Operator			1                           Laborers				0

Truck Drivers				1

Mechanic	      			6

Helpers				6

Pipe fitter

SUBCONTRACTOR PERSONNEL:  Coinserma

Foreman                                        1                    Laborers                                       4

Safety                                            1                     Skilled                                          4

Operators                                      1

- GENERAL ITEMS

  - Contacted a pressure grouting company they came to site.  We have scheduled a meeting with the grouting company this week to expedite and clarify any concerns the company may have. We need to order the grout from US, not available here.  We’ll proceed to prepare a draft order from states early next week. Ongoing

  - Prepared a quote for a change order to place fill for the crane to set the 7FA. Super Lift Kit not available. We’ll schedule a meeting with SIDOR to close this issue next Monday. Representatives of SIDOR were not available this week because of the meeting associated with the accelerated plan for CVG A. Ongoing due an answer today (4 Aug) not received as of this report.

- CLIENT ISSUES/CONCERN:

  - We issued a contract change order to Derwick for SIDOR’s request to move the fuel tank to the center of the berm (the fuel tank foundation is already partially complete). PES has been designing according to US standards, but SIDOR has requested for us to follow PDVSA standards for separation of the fuel tank and the water treatment building. This needs to be resolved by Derwick as soon as possible to avoid any impact on the project schedule. Ongoing.  Due an answer today(4 Aug) not received as of this report.

  - Need a resolution on the Change Order for back fill to allow Sidor to use the smaller crane to lift the 7FA. Due an answer today(4 Aug) not received as of this report

  - Sidor asked that we make the first pour of the 7FA fdn on Friday; it was planned to pour today, and then make second pour on Monday.  PES asked the contractor to work the next ten days, including weekends, without pause to make the loading of the cement batch plan impact a little as possible the batch plant other works.  Concorcio Megavatio replied today they will work 6 days for the 7FA only and will be ready to support a second shift next week if necessary, they will not work Sundays and will not pour Saturday.  Sidor has not replied to our request for concrete Friday morning including extra concrete trucks and three pumps.  In the meeting PES notified Sidor there is a cost associated with this acceleration, to be passed to Derwick / Sidor.

- CIVIL:

  - Ready to proceed with Water Tanks, preparing Work Orders, will send the T&C tomorrow.  Meeting set for 10:30 5 Aug to discuss the additional work and unit prices.

  - Coinserma has not responded to our request to accelerate as we expected they were informed of our displeasure and advise they will have to provide a recovery plan after tomorrow showing schedule recovery to original schedule durations.  There has been significant change in the design and they are attempting to protect their quote.  I advised we will work the quoted work where it applies and use the unit prices where there is significant change.  I also advise I will red line the changes on the original quote drawings, make a copy for the contractor, and hold the drawings for future discussion.

  - Stopped work on MH 4until Coinserma sloped excavation for MH 4, small excavator would not reach bottom so they “cheated” on the slope.

- CONCRETE FOUNDATIONS:

  - Work on the 7FA main slab with anchor bolt installation is complete for primary concrete placement. Sidor cancelled scheduled pour until August 6, 2010. Delay, Sidor has not confirmed pour 6 Aug.  Need additional QA/QC on board now for pour.

  - Work on 7FA Stack A/Bs complete except QA/QC rain delay

  - Work on 7FA Silencer ongoing should finish by week end except QA/QC rain delay

  - Backfill needed at the OWS Foundation to start the WW Tank Foundation. Rain delay and equipment not available from Site A

  - Backfill needed at the 7EA Stack Foundation. Started to prepare a Work Order. Rain delay and equipment not available from Site A

  - Ready to proceed with #100 GSU and associated Duct Banks. Started to prepare a Work Order after discussion with Bill Lugo.   Concorcio advises they will not do the duct bank immediately adjacent to the GSU and under the cable tray support.

- MECHANICAL:

  - ISI with 12 people, installing Turbine and Accessory enclosure

  - Continue with 7EA stack work

  - Will ask Concorcio to core the remaining holes for Turbine enclosure for lack of a core drill bit for our drill.

- PIPING:

  - ISI continues with prefabing of U/G piping.  Will double joint 10” FW piping

- ELECTRICAL:

  - Loaned 5,800 linear feet of PVC conduit to Site A.  We need it by Friday 6 Aug. PO for this material has been issued by Site A.

  - Still need cathodic protection general specifications and detailed design. Materials for the tanks are critical; they need to be installed before the tank erection begins.  Will start de min tank foundation no later than Monday next.

  - Coinserma excavating Manhole #4, agreed to bring new large excavator to site by today and finish MH4 and start MH5 this week.  The large excavator did not arrive.  Coinserma advised they are trying to rent a machine locally to get one to site by morning 5 Aug.

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works two shifts or a 12 hours shift

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (50%)

Complete

- Gas Turbines on Foundation (10%)

July 19, 2010 this has slipped for 7FA due to shortage of anchors, we have talked with the contractor to accelerate the schedule; he will get an official response from his home office tomorrow(?).  We think the extension, best case now, is 3 weeks or Sep 5, 2010 for 7FA

- Civil Foundations Complete (25%)

Sep 15, 2010 (*) do not have all drawings for foundations RFI 0006 issued to EDGI for forecast dates.  We will started duct bank and manhole excavation Monday Aug 2nd.  We expect at least 3 weeks delay, reviewing schedule to attempt to cut time see section 9.

- Electrical/Mechanical Complete (10%)

Dec 3, 2010 (*) expect at least 3 weeks due to lack of drawings and lack of electrical contractor, will meet with the electrical contractors next week.

- Start- up Complete and Ready to Export Power (5%)

Dec 11, 2010 (*) see above expect a revised schedule week end

The dates (*) will be revised as soon as the schedule review is complete. We expect this review is completed this week.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Nov 29, 2010

- Unit 200 – 7FA

Dec 11, 2010

- CRITICAL AREAS OF CONCERN:

  - Changes in designs are impacting project progress/completion.   Need drawings for all foundation and updated GA to meet progress milestone.  Sidor (Daniel Gonzalez) advised me they have all information for 37 of 85 foundations, for Site B, including elevations and coordinates.

  - Need finalized design, or if that cannot be completed, need to include all equipment on General Arrangement  and freeze the design with SIDOR’s approval, specially the Fuel Oil Tank, and what is effected by the change of its location.

  - Shortage of cement is affecting the scheduling of foundations.  Three day delay for pour of 7FA, as of today.

  - Material deliveries and the trickle down caused by commercial issues seriously retard our ability to execute schedule.  Received a partial list of materials on first ship, to arrive on or about 8 Aug, should be available at site no more than 1 week after.  Need to dedicate people at the port to “direct traffic” to assure Site A materials are delivered to A and vice –versa for B.

  - Need additional support from QA/QC for the pour of the 7FA slab for Friday or whenever it is poured.  Local PO placed, but “anticipo” not paid.

  - Need a procedure immed~ to assure materials are traceable from purchasing to site.  Need to resume sending the PO log or start sending a Material Tracking Report (MTR)

  - SAFETY:

    - Inclement weather, excavations

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Substation Foundations 7FA ISO phase bus(GA#22) 7FA Generator Breaker(GA#31 7FA FG Heater(GA#TBD) | TBD |  |  |
| Gas Compressors with shed, fin fans, MCC room(GA#5) | 11 August, 10 |  |  |
| 7FA CWM(GA#11) 7FA Fin Fan | 3 August, 10 5 August, 10 |  |  |
| U/G piping | 5May10 | 28May10 | Comments pending |
| GSU 7FA | 21May10, 2 Jun 10 | Need by 31 AGO |  |
| Design essentially complete | 31 May | No forecast date | No forecast date |

  - ISSUED DRAWINGS:

11. PICTURES:

Photo 1: Raw Water Pipe

Photo 2: Manhole #4

Photo 3: 7EA Filter House

Photo 4: 7EA Stack

Photo 5; 7FA Stack Foundation ready for concrete

Photo 6; 7FA Foundation ready for concrete