# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 4 September, 2010, Saturday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  90 F

RANGE: 76 to 96

SITE CONDITIONS: sunny, hot, and humid,

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Unfilled Mechanical/Piping (local ASAP)

Mark Hanks - Electrical Supt

Jose Garcia - Elect. Field Eng. (local)

Kyle Roskam - Civil Supt

Howard Velasquez-Civil Field Eng (local)

Felix Martinez-QA/QC

Jason Bird - 7EA TA (A&B)R&R

Paul Olivo – Material

Mike Montgomery-QA/QC

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila García – Translator / Doc Control (Local)

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio

General Superintendant		0

Safety					0

Foremen				0

Electricians				0

Operators				0                     Surveyor				0

Carpenters				0

Surveyor Helper			0

Oiler Helper				0

Crane Operator			0                           Laborers				0

Truck Drivers				0

Concrete Finishers			0

Oilers					0

Plumbers				0

Iron Workers				0

Helpers

Welders				0

Total:					0

SUBCONTRACTOR PERSONNEL: ISI

General Superintendant		0

Safety					1

Foremen				1

Operators				1

Oiler Helper				0

Welders                                         5

Millwrights

Crane Operator			1                           Laborers				0

Truck Drivers				1

Mechanic	      			4

Helpers				6

Pipe fitter                                       0

Total                                             22

SUBCONTRACTOR PERSONNEL:  Coinserma

Foreman                                       2		Laborers				6

Safety                                            1		Skilled					6

Operators                                      2

Welders				2		total 19

- GENERAL ITEMS

  - Have not received valuation #2 from Concorcio Megavatio to prepare a PO for last month.

  - Directed surveyors (Concorcio) to layout storm drains where possible.  PO pending

  - Crane erection for 7FA equipment. No work today

  - Consorcio Megavatio offsite today

- CLIENT ISSUES/CONCERN:

2.1   Drainage for RO Water System

2.2   Access to GSU for service (grating over containment area)

- CIVIL:

  - Ready to proceed with de min and raw Water Tanks after backfill of DB

  - Requested a quote to have Coinserma excavate for piping.  Will change to unit price PO. Quote ready, Coinserma waiting to meet with PES management

  - Ongoing duct bank near GSU 100. Instructed Coinserma to be complete in this area by Sept. 6 Concrete placement Monday Sept. 6, 2010

  - Working DB West side of MH 5 Concrete placement Monday Sept. 6, 2010

  - Preparing grout pockets for fixators, final alignment of A/Bs for Turbine on 7FA

- CONCRETE FOUNDATIONS:

4.1 No Foundation work today, contractor off site

- MECHANICAL:

  - ISI with 22 people, installing Turbine and Accessory piping and enclosures

  - Continue with 7EA stack work, review paint and prepare RFQ.  Received paint spec of originally applied paint today. Will prepare RFQ for paint.

  - Installing platforms for doors for the enclosures, need modifications

  - Installing bolts on Filter House Structure

  - Working 7FA Turbine Fixators

- PIPING:

  - Plan to start piping installation this week if we can get PO issue resolved.

  - Need a film viewer.

  - ISI continues piping installation on 7EA

  - ISI continues exhaust joint installation

  - ISI will start underground piping this week.

- ELECTRICAL:

  - Cathodic protection contractor preparing quote, should receive quote for Tanks Monday, Sept. 6 and piping Friday, Sept. 10

  - Continue preparing Cable schedule and audit of electrical drawing

  - Meggering of electrical motors near complete

- INSTRUMENTATION AND CONTROLS:

9.    SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works two shifts or a 12 hours shift (were notified both the main civil and the mechanical contractors plan to reduce overtime for commercial issues.  Will work a 48 hour week, 4 each 9 hrs days and 1 each 8 hr days.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (50%)

Complete

- Gas Turbines on Foundation (10%)

Sep 9, 2010 4 day delay Awaiting crane installation for turbine lift.  Met with Sidor to prompt them to start crane set-up.  Walked the haul road and showed where additional fill is necessary to augment the portion completed by contractor.  Probable date to set turbine is 9 Sept

- Civil Foundations Complete (25%)

Sep 15, 2010 (*) do not have all drawings for foundations.  We expect at least 5 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Dec 3, 2010 (*) expect at least 5 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Dec 11, 2010 (*) see above expect a revised schedule week end

The dates (*) will be revised as soon as the schedule review is complete and a history is trend is available.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Nov 29, 2010* expect slippage

- Unit 200 – 7FA

Dec 11, 2010

- CRITICAL AREAS OF CONCERN:

  - Commercial issues with Contractors.

  - Shortage of cement is affecting the scheduling of foundations.  I am not entertaining accelerated schedule at this time without assurance of commercial restitution.

  - .Install Site construction power, contractor received payment for other PO, have asked they use a portion to install site power. Contractor informed us he is ordering material, at least 5 days before starting installation.

  - Need to assure the 7FA has all materials, contractor support, and resources from PES to meet or shorten the schedule.  Cost for GE TA is 25K per week.

  - Crane installation and acceleration of set up schedule between turbine and generator lifts for the 7FA.

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Substation Foundations 7FA ISO phase bus(GA#22) 7FA Generator Breaker(GA#31 7FA FG Heater(GA#TBD) | TBD |  |  |
| 7FA CWM(GA#11) 7FA Fin Fan | 3 August, 10 5 August, 10 |  |  |
| U/G piping | 5May10 | 28May10 | Comments pending |
| Design essentially complete | 31 May | No forecast date | No forecast date |

11. PICTURES:

Photo 1: Final prep for concrete between #100 & GSU

Photo 2: Duct bank to High Yard and GSU