# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 07 October, 2010, Thursday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin (R&R)

TEMPERATURE:  84 F

RANGE: 78 to 94

SITE CONDITIONS: overcast, hot, humid,

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager(R&R)

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Unfilled Mechanical/Piping (local ASAP)

Unfilled mechanical / piping expat ASAP

Mark Hanks - Electrical Supt

Jose Garcia - Elect. Field Eng.

Kyle Roskam - Civil Supt

Howard Velasquez-Civil Field Eng

Felix Martinez-QA/QC

Jason Bird - 7EA TA

William McCorrmick-Safety

Paul Olivo – Material

Paul Turcott PES

Tom Koontz PES

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila García – Translator / Doc Control

SUBCONTRACTOR PERSONNEL:

Concorcio Megavatio – Civil Contractor

General Superintendant		1

Safety					1

Foremen				3

Electricians				2

Operators				4                    Surveyor				1

Carpenters				10

Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				10

Truck Drivers				4

Concrete Finishers			0

Oilers					2

Plumbers				0

Iron Workers				10

Helpers

Welders				1

Admin Support                               9

Total:					60

SUBCONTRACTOR PERSONNEL: ISI – Mechanical Contractor

General Superintendant		0

Safety					1

Foremen				1

Operators				1

Oiler Helper				0

Welders                                         6

Millwrights

Crane Operator			1                           Laborers				0

Truck Drivers				1

Mechanic	      			4

Helpers				6

Pipe fitter                                       6

Total                                             32

- GENERAL ITEMS

  - 7FA, crane disassembly stopped due to incident with 7FA.  Need to get crane disassembled and backfill removed to continue with installation. This will be done as soon as the insurance company releases SIDOR to move the crane. Crane released to move.

  - Need to review model contract and get contractors to table to formalize contracts.  We are preparing a line item scope of work for ISI, Concorcio Megavatio, and Sialca, mechanical, civil and electrical contractors respectively. Scheduled to be completed 10-8-10

  - Need status of delivery for demineralized and raw water tank materials. We are expecting from a response tomorrow. Unresolved

- CLIENT ISSUES/CONCERN:

  - Access to GSU for service (grating over containment area) Chem. grate manufacturer came to site to view GSU at Site A and prepare a quote and design. Met with the supplier and a quote is expected on Friday, Oct 8th, 2010.

  - Building design for office maintenance building, PSC, and MCC attached to compressor building; especially the admin and maintenance building that apparently has structural design issues. Communication generated to EDGI. Unresolved

  - Need crane moved at 7FA and backfill removed.  Sidor did not approve Change Order to build crane pad and subsequently remove fill, removal is in their scope of work. Crane removal on hold pending crane incident investigation. Crane released to move 10-7-10

- CIVIL:

  - Removing excess spoils from high voltage switchyard area to offsite location. Ongoing

  - Preparing a scope of work to complete Ductbanks, Manholes and Handholes. Will complete Friday

  - Reviewing drawings for new MCC location

  - Repaired broken conduits routed to #100 GSU Foundation

- CONCRETE FOUNDATIONS:

  - Placing poor concrete for Compressor Foundation 10-6-10, completed 10-7

  - Started structural fill for #100 GSU

  - Placed concrete for Raw Water Tank Foundation

  - Placed concrete for 7FA Fuel Module Pedestals and 7FA Accessory Module Pedestal Base

- MECHANICAL:

  - Paint spec. to Sedalia for review to prepare scope and RFQ.  Received a material spec, but this requires purchase of material in US and then testing to see if it is acceptable. Unresolved

  - Prepare a QA plan for tanks.  Issued scope of work for Tank PO. QA/QC plan received first draft, returned with comments. Ongoing

  - Need copy of GE drawings for 7FA. Unresolved Tom Koontz

  - Lube Oil piping installed for the 7EA Generator and Load Coupling area.

  - Welding Unit 100 exhaust Stack, installing insulation and splice plates

  - Completed erecting Unit 200 lower exhaust stack, will square up, round out and install cross braces

  - Cleaning Unit 100 Oil Resevoirs with cleaning solvent

  - Preparing to install Jacking Post for Unit 200 Generator and place back on centerline

- PIPING:

  - Need a film viewer.  Will purchase US not available here, they read film with flashlight.  Have doubts to the veracity of the x-ray readings. Expecting Cole Franklin to bring one back from the US when he comes back from R &R.

  - ISI continued underground piping this week.  Fabbing spools for tie points.  Preparing ISO’s from drawings produced at site. Ongoing

- ELECTRICAL:

  - Prepared a scope of work for electrical contract with local contractor, about 90% complete.

  - Met Cathodic Protection Contractor to clarify scope of work previously quoted

- INSTRUMENTATION AND CONTROLS:

9.    SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works two shifts or a 12 hours shift.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (60%)

Complete

- Civil Foundations Complete (25%)

Sep 15, 2010 (*) do not have all drawings for foundations.  We expect at least 7 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Early 2011 (*) expect at least 7 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Early 2011 (*) will issue new dates after acceptance or rejection of CO

The dates (*) will be revised as soon as the schedule review is complete, the 7EA generator and crane collision incident is resolved.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Early  2011* expect slippage

- Unit 200 – 7FA

Early  2011

- CRITICAL AREAS OF CONCERN:

  - Crane move for 7FA generator This will be a total of four  week delay with associated cost exceeding $100K

  - Building design.  Three engineers have reviewed building design, is not suitable.  Need the designer to come to site sit with Sidor and/or set up a conference call to resolve this or modifications will be done to buildings which will be back charged to the building supplier. We are in the process of issuing a communication with suggested solutions to the design problems for the admin and warehouse building shortly..Unresolved

  - Need to assure the 7FA has all materials, contractor support, and resources from PES to meet or shorten the schedule.  Cost for GE TA is 25K per week.  GE Tech arrived at the CVG B site today for inspection of 7FA Generator damage. Crane released to move, initial inspection of external components started.GE TA provided pictures and comments associated with the generator damaged to GE main office for review and recommended actions

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Substation Foundations 7FA ISO phase 7FA Generator Breaker(GA#31 7FA FG Heater | TBD |  |  |

11; Pictures

7FA Crane Damage

7FA Crane Damage

7FA Crane Damage

7FA Exhaust Stack

7FA Accessory Module Foundation