# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 1 November, 2010, Monday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  94 F

RANGE: 76 to 96

SITE CONDITIONS: overcast, rain

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Unfilled  - Scheduler (A&B)

Unfilled Mechanical/Piping local ASAP

Unfilled mechanical / piping expat ASAP

Unfilled - Electrical Supt

Jose Garcia - Elect. Field Eng.

Unfilled - Civil Supt

Howard Velasquez-Civil Field Eng

Unfilled -QA/QC

Jason Bird - 7EA TA

Unfilled -Safety

Paul Olivo – Material

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Unfilled -Logistics (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila García – Translator / Doc Control

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio – Civil Contractor

General Superintendant		1

Safety					1

Foremen				1

Supervisors				0

Electricians				0

Operators				0                   Surveyor				0

Carpenters				5

Surveyor Helper			0

Oiler Helper				0

Crane Operator			0                           Laborers				0

Truck Drivers				1

Concrete Finishers			0

Oilers					0

Plumbers				0

Iron Workers				3

Helpers				2

Welders				0

Admin Support                               0

Total:					9

SUBCONTRACTOR PERSONNEL: ISI – Mechanical Contractor

General Superintendant		0 		Supervisor				0.

Coordinator				1		Safety					1

Foremen				0		Operators				0

Oiler Helper				0 		Welders                                         0

Millwrights			   	0		Crane Operator			1

Laborers				0		Truck Drivers				1

Mechanic	      			0		Helpers				6

Pipe fitter                                       0		Total                                             8

- GENERAL ITEMS

  - GE TA as well as PES personnel reviewed generator damage and issue initial report to GE main office. Waiting for GE formal response.   Attempted to connect to GE conference call power outages made connection impossible.  Have had multiple power outages today, durations up to 3 hours.

  - Need status of delivery for de mineralized and raw water tank materials, and Cathodic protection materials purchased by Sedalia. We are expecting a response tomorrow. Material not available, now awaiting Cathodic protection and tank material to start tank erection

  - Sidor to produce floor plan for office area for Admin Bldg by Oct. 27 received CAD drawings.  Prepared lighting take off.

- CLIENT ISSUES/CONCERN:

  - Building design for office maintenance building apparently has structural design issues. Communication generated to EDGI. Prepared a list of questions presented same.   Unresolved

  - Oil flush is completed as of 26 Oct, no report received.

  - Small crew Client concerned for progress

- CIVIL:

  - Concorcio advises they will accept a letter directing work for GSU 100 and Compressor Fdn, will include this work into contract.  Will work a small crew only on the previously agreed fdns.  7EA fuel module, 7EA L.O. demister, compressors, GSU 100, HM6, and possible two sections of unfinished duct bank for 7EA.

- CONCRETE FOUNDATIONS:

  - We will collect cost for CO for additional QA/QC cost to oversee batch plants (due to Felix  Martinez being on R&R and past history with concrete here) for Compressor foundation.

  - 100 GSU foundation, forms and rebar being prepared

  - Working compressor second pour only.

- MECHANICAL:

  - 7EA oil flush completed quality is very good.  Will prepare a critique of the flushing procedure results for further reference.

  - Clean and protect piping for 7FA both in lay down yard and at machine.

  - Removing materials not installed from site to lay down Yard.

  - Need to know status of the Raw and De-min water tank materials (rolled shell plates, top plates, and bottom plates.  De-min presently in fabrication, raw water to ship on next ship, expect delivery at site no earlier than 3 weeks.

- PIPING:

  - Restoring L.O. piping after oil flush and installing permanent gauges, fixtures, and gaskets.  Clean spilled oil from 7 EA fdn.

- ELECTRICAL:

  - Reviewing drawings, preparing pulling schedule for 7EA.

  - Need to return cables taken from B for use at A

  - Moved MCCs to area to open and inspect and verify the delivered equipment meets the drawing and specifications.  Hold for electricians

  - Need remaining Cathodic protection equipment.

- INSTRUMENTATION AND CONTROLS:

8.1 Need Cathodic panels and dwgs.

8.2 Met with PES DCS people tomorrow regarding controls, need to explain to Sidor they are not getting a DCS system.

9.    SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works long shifts.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (60%)

Complete

- Civil Foundations Complete (25%)

Nov 15, 2010 (*) do not have all drawings for foundations.  We expect at least 9 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Early 2011 (*) expect at least 9 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Early 2011 (*) will issue new dates after acceptance or rejection of CO

The dates (*) will be revised as soon as the schedule review is complete, the 7EA generator and crane collision incident is unresolved.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Early  2011* expect slippage

- Unit 200 – 7FA

Early  2011

- CRITICAL AREAS OF CONCERN:

  - Building design.  Three engineers have reviewed building design, is not suitable.  Need the designer to come to site sit with Sidor and/or set up a conference call to resolve this or modifications will be done to buildings which will be back charged to the building supplier. We are in the process of issuing a communication with suggested solutions to the design problems for the admin and warehouse building shortly..Unresolved

  - GE required more pictures with comments in GE main office for review and recommended actions.  Delivered photos no comments received. Ongoing

  - Moved 7FA Generator to free A/Bs, topographer verified location after incident to compare to original location. Documentation received, PO for NDE examination of anchor bolts for 7FA generator prepared.

  - Need to jack up the generator to check anchor bolts hold for additional craft personnel, possible next week.

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Substation Foundations 7FA ISO phase 7FA Generator Breaker(GA#31 7FA FG Heater | TBD |  |  |

11. Pictures

Photo 1: MH 6 mud mat pour

Photo 2: 10 min rain

Photo 3: 15 min rain