# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 11 November, 2010, Thursday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  89 F

RANGE: 74 to 94

SITE CONDITIONS: overcast, hot, and humid

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Unfilled - Scheduler (A&B)

Unfilled Mechanical/Piping local ASAP

Unfilled mechanical / piping expat ASAP

Unfilled - Electrical Supt

Jose Garcia - Elect. Field Eng.

Unfilled - Civil Supt

Howard Velasquez-Civil Field Eng

Unfilled -QA/QC

Jason Bird - 7EA TA

Unfilled -Safety

Paul Olivo – Material

MATERIAL SUPPORT:

José Angel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Unfilled -Logistics (Local)

Paola Gómez – Administration (Local)

Patricia Muños – Administration (Local)

Skeila García – Translator / Doc Control

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio – Civil Contractor

General Superintendant		1

Safety					1

Foremen				1

Supervisors				2

Electricians				1

Operators				0                   Surveyor				1

Carpenters				6

Surveyor Helper			2

Oiler Helper				0

Crane Operator			1                           Laborers				1

Truck Drivers				1

Concrete Finishers			4

Oilers					0

Plumbers				1

Iron Workers				0

Helpers				0

Welders				1

Admin Support                               7

Total:					31

SUBCONTRACTOR PERSONNEL: ISI – Mechanical Contractor

General Superintendant		0 Supervisor				1

Coordinator				1 Safety					1

Foremen				0 Operators				0

Oiler Helper				0 Welders                                         0

Millwrights			   	0 laborers				0 Crane Operator			1 Truck Drivers				1

Mechanic	      			0	 Helpers				6

Pipe fitter                                       0 Total                                              10

- GENERAL ITEMS

  - No internet at site again, we have called the provider for weeks and they have not arrived to effect repairs/modification.  I called another provider presently providing the service at El Furrial.  They will quote on installing a comparable system here.

  - Prepare for Monday 15 Nov concrete pour for compressor fdn second pour, third party QA to check tomorrow before pour.  This is a 9 day delay

  - Received pipe not sandblasted and primed, will have ISI prepare a quote for moving the pipe, sandblasting and priming the pipe.  Will back charge purchasing.

  - GE TA as well as PES personnel reviewed generator damage and issue initial report to GE main office. Received response GE wants to remove fan housing and check frame for cracks.  Will need to remobilize crew and GE TA after NDE of bolts, Presently no schedule to remobilize GE

  - Need status of delivery for de mineralized and raw water tank materials, and cathodic protection materials purchased by Sedalia. We are expecting a response tomorrow. Material not available, now awaiting Cathodic protection and tank material to start tank erection

  - Preparing quote for de scope liquid fuel.  Reviewing received  materials.

- CLIENT ISSUES/CONCERN:

  - Building design for office maintenance building apparently has structural design issues. Communication generated to EDGI. Prepared a list of questions presented same.   Unresolved awaiting response by mail?

  - Small crew Client concerned for progress.

- CIVIL:

  - Delays for contractors entering site due to labor problems.

  - Concorcio will work a small crew only on the previously agreed fdns.  7EA fuel module, 7EA L.O. demister, compressors, GSU 100, HM6, and possible two sections of unfinished duct bank for 7EA.

  - Forming compressor MCC bldg

  - Forming and installing rebar GSU 100

- CONCRETE FOUNDATIONS:

  - We will collect cost for CO for additional QA/QC cost to oversee batch plants (due to Felix Martinez being on R&R and past history with concrete here) for Compressor foundation.

  - Working compressor second pour. No concrete expected 15Nov

- MECHANICAL:

  - 7EA oil flush completed quality is very good.  Will prepare a critique of the flushing procedure results for further reference.  Still no final report from Venefilter on flushing.  I told Venefilter’s supervisor last week I will not sign their invoice to release for payment without final report.

  - Foundations ready to erect tanks, awaiting material delivery.  The material delivery for Cathodic and tank material is still an issue.

  - Jacking 7FA generator to block up for NDE of anchor bolts, hope to finish before Friday.  We have been told mechanical contractor will not return next week due to lack of payment.

  - Working punch list 7EA with small crew.

- PIPING:

  - Cleaning spilled oil from 7 EA fdn after L.O. flush.  Need materials ie.. simple orange or green degreaser, ordered not received

- ELECTRICAL:

  - Need to return cables taken from B for use at A

  - Moved MCCs to area to open and inspect and verify the delivered equipment meets the drawing and specifications.  Hold for electricians prepared PO for issue?

  - Moving additional MCCs to R5 area.

  - Need remaining cathodic protection equipment.  Did not arrive with last shipment!

- INSTRUMENTATION AND CONTROLS:

8.1 Need cathodic panels and dwgs.

- SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works long shifts.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (60%)

Complete

- Civil Foundations Complete (25%)

Nov 15, 2010 (*) do not have all drawings for foundations.  We expect at least 9 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Early 2011 (*) expect at least 9 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Early 2011 (*) will issue new dates after acceptance or rejection of CO

The dates (*) will be revised as soon as the schedule review is complete, the 7EA generator and crane collision incident is unresolved.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Early 2011* expect slippage

- Unit 200 – 7FA

Early 2011

- CRITICAL AREAS OF CONCERN:

  - Building design.  Three engineers have reviewed building design, is not suitable.  Need the designer to come to site sit with Sidor and/or set up a conference call to resolve this or modifications will be done to buildings which will be back charged to the building supplier. We are in the process of issuing a communication with suggested solutions to the design problems for the admin and warehouse building shortly.Unresolved awaiting documents sent via FED EX having them picked up in Valencia to deliver to site.

  - Moving 7FA Generator to free A/Bs, PO for NDE examination of anchor bolts for 7FA generator prepared.

  - The list of materials previously generated, is all material on order?

  - Send lighting BOM for order in US, prepared local PO for materials available at site, will send classified area lighting request to Sedalia.

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Substation Foundations 7FA ISO phase 7FA Generator Breaker(GA#31 7FA FG Heater | TBD |  |  |

- Pictures No new photos, due to unscheduled exit

Photo 1: Compressor bldg MCC rebar ongoing.

Photo 3: GSU 100 ongoing