# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 11 September, 2010, Saturday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  90 F

RANGE: 76 to 96

SITE CONDITIONS: sunny, hot, and humid, poor air quality

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Unfilled Mechanical/Piping (local ASAP)

Mark Hanks - Electrical Supt

Jose Garcia - Elect. Field Eng. (local)

Kyle Roskam - Civil Supt

Howard Velasquez-Civil Field Eng (local)

Felix Martinez-QA/QC

Jason Bird - 7EA TA (A&B) R&R

Paul Olivo – Material

Mike Montgomery-QA/QC

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila García – Translator / Doc Control (Local)

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio off site

General Superintendant		0

Safety					1

Foremen				1

Electricians				0

Operators				0                     Surveyor				0

Carpenters				5

Surveyor Helper			0

Oiler Helper				0

Crane Operator			0                           Laborers				3

Truck Drivers				0

Concrete Finishers			0

Oilers					0

Plumbers				0

Iron Workers				5

Helpers

Welders				0

Total:					15

SUBCONTRACTOR PERSONNEL: ISI

General Superintendant		0

Safety					1

Foremen				1

Operators				1

Oiler Helper				0

Welders                                         5

Millwrights

Crane Operator			1                           Laborers				0

Truck Drivers				1

Mechanic	      			4

Helpers				6

Pipe fitter                                       0

Total                                             22

SUBCONTRACTOR PERSONNEL:  Coinserma

Foreman                                       2		Laborers				6

Safety                                            1		Skilled					6

Operators                                      2

Welders				2		total 19

- GENERAL ITEMS

  - Set 7FA turbine.  See attached photos. Went well.

  - Awaiting valuation #2 from Concorcio Megavatio again.  Need new copy of valuation corrected to prepare a PO for last month.

  - Directed surveyors (Concorcio) to layout storm drains where possible,

  - Discussed fill removal for the office and maintenance building, with Concorcio and Coinserma.  Sidor has located a spot to place surplus fill, Concorcio to give quote for removal.  Quote received today.  Will issue PO when we have hours.

- CLIENT ISSUES/CONCERN:

  - 2.1   Drainage for RO Water System, study prepared must be rerouted to North to miss duct banks.

2.2   Access to GSU for service (grating over containment area) Check Chemical Grate, cost will be prohibitive.  Will prepare quote for Sidor.  Received brochure for materials.

- CIVIL:

  - Concorcio agreed surveyed the location for De-min tank, but no excavation machinery to start excavations.  Off work today

  - Received drawings to prepare liquid Fuel De Scope documents.

  - Received unit pricing from Coinserma to excavate for piping.  Plan to de-mob Coinserma.

- CONCRETE FOUNDATIONS:

4.1 start excavation for de min water tank possible Monday and GSU excavation immediately after.

4.2 Prepare a list of fdn priorities for Concorcio; they will be fully mobilized by sometime next week, prepared list and issued PO for initial work.  PO idea is only a temporary solution, need to issue contract for all remaining work to control cost better.

- MECHANICAL:

  - ISI with 22 people, installing 7EA Turbine and Accessory piping and start installing steel below turbine before setting 7FA turbine

  - Continue with 7EA stack weld, sent paint spec. to Sedalia for review to prepare scope and RFQ.  Received a material spec, but this requires purchase of material in US and then testing to see if it is acceptable.

  - Installing bolts on Filter House Structure, awaiting delivery of correct bolts.  Scheduled delivery now Monday.  Will plan to QA the filter house Tuesday.

  - Prepare a QA plan for tanks.

- PIPING:

  - Piping installation is started, but NCR issued for materials..

  - Need a film viewer.  Will purchase locally.

  - ISI continues piping installation on 7EA

  - ISI continues exhaust joint installation

  - ISI will start underground piping this week.  Fab spools for tie points.  Preparing ISO’s from drawings produced at site.

- ELECTRICAL:

  - Cathodic protection contractor, received quote for Tanks Monday, Sept. 6 and piping is scheduled for Friday, Sept. 10, not received at this writing.

  - Cable schedule for hi and med voltage cables completed.  Doing review against received.  Will send shortage list to determine what can be ordered here, and what is ordered by Sedalia.  Original take off was not as good a swe thought, some cables missed.

  - Review and audit of electrical drawing against equipment nomenclature tags ongoing, all transformers checked will check motors.

- INSTRUMENTATION AND CONTROLS:

9.    SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works two shifts or a 12 hours shift.  Need authorization to work more hours.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (50%)

Complete

- Gas Turbines on Foundation (10%)

Sep 11, 2010 7 day delay Awaiting crane installation for turbine lift.  Set turbine, 7 day delay to GE TA @25K per day.

- Civil Foundations Complete (25%)

Sep 15, 2010 (*) do not have all drawings for foundations.  We expect at least 5 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Dec 3, 2010 (*) expect at least 5 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Dec 11, 2010 (*) see above expect a revised schedule week end

The dates (*) will be revised as soon as the schedule review is complete and a history is trend is available.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Nov 29, 2010* expect slippage

- Unit 200 – 7FA

Dec 11, 2010

- CRITICAL AREAS OF CONCERN:

  - Commercial issues with Contractors.

  - Shortage of cement is affecting the scheduling of foundations.  I am not entertaining accelerated schedule at this time without assurance of commercial restitution.  Lost 2 days this week for lack of sand to make concrete, for 7FA diffuser foundation and for 7FA accy module and liquid fuel module.

  - .Install Site construction power, contractor has placed transformers, completed fence, and installed distribution panel.  Need an outage to connect power.  Sidor advised today they will not take an outage due to Site A constraints.

  - Need to assure the 7FA has all materials, contractor support, and resources from PES to meet or shorten the schedule.  Cost for GE TA is 25K per week.

  - Crane installation and acceleration of set up schedule between turbine and generator lifts for the 7FA.  Crane people left site immediately after setting turbine, need them to work 7 days to disassemble crane and reassemble.  Will talk to Concorcio to start  backfill for second lift.  Hopefully this will be under our direction based on the fiasco associated with first lift.

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Substation Foundations 7FA ISO phase 7FA Generator Breaker(GA#31 7FA FG Heater | TBD |  |  |
| 7FA Fin Fan | 5 August, 10 |  |  |
| U/G piping | 5May10 | 28May10 | Prepared dwgs in field |
| Design essentially complete | 31 May | No forecast date | No forecast date |

- PICTURES:

Photo 1: 7EA turbine on fdn

Photo 2: 7FA turbine over bolts

Photo 3: 7FA nice slow and level

Photo 4: 7FA turbine picked level