# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 13 November, 2010, Saturday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  89 F

RANGE: 74 to 94

SITE CONDITIONS: overcast, hot, and humid

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Unfilled - Scheduler (A&B)

Unfilled Mechanical/Piping local ASAP

Unfilled mechanical / piping expat ASAP

Unfilled - Electrical Supt

Jose Garcia - Elect. Field Eng.

Unfilled - Civil Supt

Howard Velasquez-Civil Field Eng

Unfilled -QA/QC

unfilled - 7EA TA

Unfilled -Safety

Unfilled  – Material

MATERIAL SUPPORT:

José Angel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Unfilled -Logistics (Local)

Paola Gómez – Administration (Local)

Patricia Muños – Administration (Local)

Skeila García – Translator / Doc Control

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio – Civil Contractor

General Superintendant		1

Safety					1

Foremen				1

Supervisors				2

Electricians				1

Operators				0                   Surveyor				1

Carpenters				6

Surveyor Helper			2

Oiler Helper				0

Crane Operator			1                           Laborers				1

Truck Drivers				1

Concrete Finishers			4

Oilers					0

Plumbers				1

Iron Workers				0

Helpers				0

Welders				1

Admin Support                               7

Total:					31

SUBCONTRACTOR PERSONNEL: ISI – Mechanical Contractor

Total                                              0

- GENERAL ITEMS

  - Power was cut at 9:00 Am today by Sidor.  It will be off for 6 or more hours.  We must pay the crew that is here to prepare the pour for Monday all day.

  - We were asked to provide an office for the Armed National Guard, I advised Sidor’s rep this is in their scope, but I can provide a temporary container for the guard.  Sidor has connected power to the container we prepared for use as storage of electrical/electronics material.  Sidor asked for the key to the office, I did not give them.  I was asked by Sidor’s people when we will abandon the site so guard can lock it up!!!

  - Received notice late yesterday no concrete for Monday, we are working Saturday to be ready for early Monday pour of compressor building.  This is a 9 plus day delay

  - We have repaired the internet at site.  Jose stayed on the phone for about 3 hours to correct.  I have called another provider they will quote on installing a serviceable system here.

  - Received pipe not sandblasted and primed, will have ISI prepare a quote for moving the pipe, sandblasting and priming the pipe.  Will back charge purchasing.

  - GE reviewed generator damage and issued response GE wants to remove fan housing and check frame for cracks.  Will need to remobilize crew and GE TA after NDE of bolts, Presently no schedule to remobilize GE, no mechanical contractor next week

  - Need status of delivery for de mineralized and raw water tank materials, and cathodic protection materials purchased by Sedalia. We are expecting a response tomorrow. Material not available, now awaiting Cathodic protection and tank material to start tank erection

  - Preparing quote for de scope liquid fuel.  Reviewing received  materials.

- CLIENT ISSUES/CONCERN:

  - Building design for office maintenance building apparently has structural design issues. Communication generated to EDGI. Prepared a list of questions presented same.   Received FED EX package finally from Valencia.  This information is supposedly sufficient to satisfy client.  We will present it in raw form and let Sidor accept or deny.

  - Small crew Client concerned for progress.

- CIVIL:

  - Delays for contractors entering site due to labor problems.

  - Concorcio will work a small crew only on the previously agreed fdns.  7EA fuel module, 7EA L.O. demister, compressors, GSU 100, HM6, and possible two sections of unfinished duct bank for 7EA.

  - Compressor MCC bldg ready for concrete No concrete available we are advised after we are working Saturday to be ready for early Monday pour.

  - Compressor fdn ready for second pour except cleaning inside forms No concrete available we are advised after we are working Saturday to be ready for early Monday pour.

  - Forming and installing rebar GSU 100

  - Third party QA today and Monday for Compressor pour.

- CONCRETE FOUNDATIONS:

  - We will collect cost for CO for additional QA/QC cost to oversee batch plants (due to Felix Martinez being on R&R and past history with concrete here) for Compressor foundation.

  - Working GSU 100

- MECHANICAL:

  - 7EA oil flush completed quality is very good.  Will prepare a critique of the flushing procedure results for further reference.  Still no final report from Venefilter on flushing.  I told Venefilter’s supervisor last week I will not sign their invoice to release for payment without final report.

  - Foundations ready to erect tanks, awaiting material delivery.  The material delivery for Cathodic and tank material is still an issue.

  - Jacking 7FA generator to block up for NDE of anchor bolts, hope to finish today.  We have been told mechanical contractor will not return next week due to lack of payment.

  - Working punch list 7EA with small crew.

- PIPING:

  - Cleaning spilled oil from 7 EA fdn after L.O. flush.  hold for materials

- ELECTRICAL:

  - Need to return cables taken from B for use at A

  - Moved MCCs to area to open and inspect and verify the delivered equipment meets the drawing and specifications.  Hold for electricians prepared PO for issue?

  - Moving additional MCCs to R5 area from A.

  - Need remaining cathodic protection equipment.  Did not arrive with last shipment!

- INSTRUMENTATION AND CONTROLS:

8.1 Need cathodic panels and dwgs.

8.2 Jose checking major electrical material against drawings

- SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works long shifts.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (60%)

Complete

- Civil Foundations Complete (25%)

Nov 15, 2010 (*) do not have all drawings for foundations.  We expect at least 9 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Early 2011 (*) expect at least 9 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Early 2011 (*) will issue new dates after acceptance or rejection of CO

The dates (*) will be revised as soon as the schedule review is complete, the 7EA generator and crane collision incident is unresolved.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Early 2011* expect slippage

- Unit 200 – 7FA

Early 2011

- CRITICAL AREAS OF CONCERN:

  - Building design.  Need the designer to come to site sit with Sidor and/or set up a conference call to resolve this or modifications will be done to buildings which will be back charged to the building supplier.Unresolved awaiting documents sent via FED EX having them picked up in Valencia to deliver to site.

  - Moving 7FA Generator to free A/Bs, PO for NDE examination of anchor bolts for 7FA generator prepared.

  - The list of materials previously generated, is all material on order?

  - Send lighting BOM for order in US, prepared local PO for materials available at site, will send classified area lighting request to Sedalia.

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

- Photos

Photo 1: 7EA stack ready for groutPhoto 2: 7FA status.

Photo 3: 7EA GSU form and rebar

Photo 4: MH 6 base status

Photo 5: 7EA platform mods required