# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 15 September, 2010, Wednesday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  98 F

RANGE: 78 to 98

SITE CONDITIONS: hot, humid

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Unfilled Mechanical/Piping (local ASAP)

Mark Hanks - Electrical Supt

Jose Garcia - Elect. Field Eng. (local)

Kyle Roskam - Civil Supt

Howard Velasquez-Civil Field Eng (local)

Felix Martinez-QA/QC

Jason Bird - 7EA TA (A&B)

Paul Olivo – Material

Mike Montgomery-QA/QC

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila García – Translator / Doc Control (Local)

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio

General Superintendant		0

Safety					1

Foremen				1

Electricians				0

Operators				0                     Surveyor				0

Carpenters				5

Surveyor Helper			0

Oiler Helper				0

Crane Operator			0                           Laborers				3

Truck Drivers				0

Concrete Finishers			0

Oilers					0

Plumbers				0

Iron Workers				5

Helpers

Welders				0

Total:					15

SUBCONTRACTOR PERSONNEL: ISI

General Superintendant		0

Safety					1

Foremen				1

Operators				1

Oiler Helper				0

Welders                                         5

Millwrights

Crane Operator			1                           Laborers				0

Truck Drivers				1

Mechanic	      			4

Helpers				6

Pipe fitter                                       0

Total                                             22

SUBCONTRACTOR PERSONNEL:  Coinserma

Foreman                                       2		Laborers				6

Safety                                            1		Skilled					6

Operators                                      2

Welders				2		total 19

- GENERAL ITEMS

  - Concorcio again did not mobilize.  They asked our forbearance, but are occupied in A, promised to start back fill of 7FA tomorrow in the Contractor meeting today.

  - Received valuation #2 from Concorcio Megavatio again.  Reviewed found one error asked them to accept short paying this one item.

  - Directed surveyors (Concorcio) to layout storm drains where possible, they will be available at site after noon tomorrow.

  - Discussed fill removal for the office and maintenance building, with Concorcio and Coinserma.  Sidor has located a spot to place surplus fill, Concorcio to give quote for removal.  Quote received.  Will issue PO when we have hours.

  - Concorcio cast concrete protection beams for 7FA anchor bolts to be straddled by Crane for Generator setting.

  - Completed installation and grout of fixators for 7FA.

  - Dual fuel team working on 7EA.  Pipe repairs to pre fabbed spools, need QA/QC for work performed in Sedalia, no NDE reports.

- CLIENT ISSUES/CONCERN:

  - Drainage for RO Water System, study prepared must be rerouted to North to miss duct banks.   Spoke to EDGI we will red line a drawings and continue.

2.2   Access to GSU for service (grating over containment area) Check Chemical Grate, cost will be prohibitive.  Will prepare quote for Sidor.  Received brochure for materials.

- CIVIL:

  - Concorcio agreed and surveyed the location for De-min tank, but no excavation machinery to start excavations.

  - Received drawings to prepare liquid Fuel De Scope documents.  Have stopped the work, but have not completed mark up.

  - Received Coinserma plan for the remaining work and we will review and determine if there is any reason to continue with them.

- CONCRETE FOUNDATIONS:

4.1 start excavation for de min water tank probable next Monday and GSU excavation immediately after.

4.2 Prepare a list of fdn priorities for Concorcio; they will be fully mobilized by sometime this week (today we are notified probably next Monday), prepared list and issued PO for initial work.  PO idea is only a temporary solution, need to issue contract for all remaining work to control cost better.

- MECHANICAL:

  - ISI with 22 people, installing 7EA Turbine and Accessory piping

  - Installed steel below 7FA turbine for inlet plenum

  - Continue with 7EA stack weld, sent paint spec. to Sedalia for review to prepare scope and RFQ.  Received a material spec, but this requires purchase of material in US and then testing to see if it is acceptable.

  - Installing bolts on Filter House Structure, received correct bolts.  Scheduled completion Thursday.  Will plan to QA the filter house after.

  - Prepare a QA plan for tanks.  Issued scope of work for Tank PO.

- PIPING:

  - Piping installation is started, but NCR issued for materials.  Received PES QA Plan and find MTR required per plan.

  - Need a film viewer.  Will purchase locally.

  - ISI continues piping installation on 7EA

  - ISI will start underground piping this week.  Fab spools for tie points.  Preparing ISO’s from drawings produced at site.

- ELECTRICAL:

  - Cathodic protection contractor, received quote for Tanks Monday, Sept. 6 and piping is scheduled for Friday, Sept. 10, not received at this writing.  Will call to remind them tomorrow

  - Cable schedule for hi and med voltage cables completed.  Received list of cables to be rerouted to A.

  - Review and audit of electrical drawing against equipment nomenclature tags ongoing, all transformers checked will check motors and additional materials as received.

- INSTRUMENTATION AND CONTROLS:

9.    SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works two shifts or a 12 hours shift.  Need authorization to work more hours.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (60%)

Complete

- Civil Foundations Complete (25%)

Sep 15, 2010 (*) do not have all drawings for foundations.  We expect at least 7 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Dec 3, 2010 (*) expect at least 5 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Dec 11, 2010 (*) see above expect a revised schedule week end

The dates (*) will be revised as soon as the schedule review is complete and a history is trend is available.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Nov 29, 2010* expect slippage

- Unit 200 – 7FA

Dec 11, 2010

- CRITICAL AREAS OF CONCERN:

  - Commercial issues with Contractors.

  - Shortage of cement is affecting the scheduling of foundations.  We will advise when we require cement, Sidor must provide.

  - Install Site construction power, contractor has placed transformers,         completed fence, and installed distribution panel.  Need an outage to connect power.  Outage to tie in planned for tomorrow morning.

  - Need to assure the 7FA has all materials, contractor support, and resources from PES to meet or shorten the schedule.  Cost for GE TA is 25K per week.

  - Crane installation and acceleration of set up schedule between turbine and generator lifts for the 7FA.  Talked to Concorcio to start backfill for second lift original scope, will prepare a PO if necessary.  Hopefully this will be under our direction based on the fiasco associated with first lift.  No progress on back fill.  Crane delay for dismantling and moving.  This will have an impact on schedule unless it starts tomorrow.

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Substation Foundations 7FA ISO phase 7FA Generator Breaker(GA#31 7FA FG Heater | TBD |  |  |
| 7FA Fin Fan | 5 August, 10 |  |  |
| U/G piping | 5May10 | 28May10 | Prepared dwgs in field |
| Design essentially complete | 31 May | No forecast date | No forecast date |

- PICTURES:

Photo 1: 7FA crane anchor bolts protection

Photo 2: 7EA stub ups

Photo 3: 7EA GAC duct bank

Photo 4: 7FA Gen fixators grouted