# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 17 November, 2010, Wednesday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  87 F

RANGE: 74 to 93

SITE CONDITIONS: Rain, hot, and humid

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Unfilled - Scheduler (A&B)

Unfilled Mechanical/Piping local ASAP

Unfilled mechanical / piping expat ASAP

Unfilled - Electrical Supt

Jose Garcia - Elect. Field Eng.

Unfilled - Civil Supt

Howard Velasquez-Civil Field Eng

Unfilled -QA/QC

unfilled - 7EA TA

Unfilled -Safety

Unfilled  – Material

MATERIAL SUPPORT:

José Angel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Unfilled -Logistics (Local)

Paola Gómez – Administration (Local)

Patricia Muños – Administration (Local)

Skeila García – Translator / Doc Control

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio – Civil Contractor

General Superintendant		1

Safety					1

Foremen				2

Supervisors				4

Electricians				1

Operators				3                   Surveyor				1

Carpenters				12

Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                          Laborers				1

Truck Drivers				1

Concrete Finishers			7

Oilers					0

Plumbers				1

Iron Workers				2

Helpers				8

Welders				1

Admin Support                               7

Total:					54

SUBCONTRACTOR PERSONNEL: ISI – Mechanical Contractor

Total                                              0

- GENERAL ITEMS

  - We have provided a temporary container for the guard.  Sidor has provided cable and we have connected power to the container.

  - Called internet provider again no tech arrived, this is about 3 months with this problem.  The provider before talked Daniel F through checking the system and declared we had no problems.  They checked again and indicate that we have about 25% of capacity that we are paying for and this is acceptable by their standards.  They made the mistake of sending a print out of the testing and results, even I can understand.  The provider says we did not purchase maintenance, for the price we pay we should have 24 hr technicians.  We plan to change service provider if the new quote is even close to what we are paying.  1 hour to send daily report is unacceptable; my attention span is not that long.

  - Received notice concrete available Thursday at 5AM.

  - Received pipe not sandblasted and primed, will have ISI prepare a quote for moving the pipe, sandblasting and priming the pipe.  Will back charge purchasing.

  - GE reviewed generator damage and issued response GE wants to remove fan housing and check frame for cracks.  Will need to remobilize crew and GE TA after NDE of bolts, Presently no schedule to remobilize GE, no mechanical contractor next week

  - Need status of delivery for de mineralized and raw water tank materials, and cathodic protection materials purchased by Sedalia. We are expecting a response tomorrow. Material not available, now awaiting Cathodic protection and tank material to start tank erection

  - Preparing quote for de scope liquid fuel.  Reviewing received  materials hold.

- CLIENT ISSUES/CONCERN:

  - Building design for office maintenance building apparently has structural design issues. Received FED EX package finally from Valencia.  We reviewed the material and find it insufficient.  Howard has created a report without blame but, showing where the assumptions are not realistic.  I suggest we turn it over to Sidor and allow them to decide.  Sidor earlier advised if the design is not acceptable and not corrected they will modify the buildings to meet the requirements to our expense.

  - Cement availability for continuing concrete pours.

- CIVIL:

  - Concorcio will work a small crew only on the previously agreed fdns.  7EA fuel module, 7EA L.O. demister, compressors, GSU 100, HM6, and possible two sections of unfinished duct bank for 7EA.

  - Compressor MCC bldg ready for concrete No concrete available

  - Compressor fdn ready for second pour except cleaning inside form  No concrete

  - GSU 100 probable for Thurs first pour

  - Third party QA will have them return Thursday.

- CONCRETE FOUNDATIONS:

  - Met with Sidor this morning regarding concrete.  They will provide concrete using cold water early in the morning of Thursday but without ice due to machinery break down.  This is the only contingency plan available at this time.

  - We will collect cost for CO for additional QA/QC cost to oversee batch plants (due to Felix Martinez being on R&R and past history with concrete here) for Compressor foundation.

  - Working GSU 100

  - Working MH 6

  - Working 7FA liq and accy module retaining walls forms

  - Working 7EA fuel gas module

  - Working PEECC to MH 1 ductbank excavation

- MECHANICAL:

  - 7EA oil flush completed quality is very good.  Will prepare a critique of the flushing procedure results for further reference.  Still no final report from Venefilter on flushing.  I told Venefilter’s supervisor last week I will not sign their invoice to release for payment without final report.

  - Foundations ready to erect tanks, awaiting material delivery.  The material delivery for Cathodic and tank material is still an issue.

- PIPING:

  - No work

- ELECTRICAL:

  - Need to return cables taken from B for use at A

  - Moved MCCs to area to open and inspect and verify the delivered equipment meets the drawing and specifications.  PO prepared for issue

  - Moving additional MCCs to R5 area from A.

  - Need remaining cathodic protection equipment.  Did not arrive with last shipment!

- INSTRUMENTATION AND CONTROLS:

8.1 Need cathodic panels and dwgs.

8.2 Jose checking major electrical material against drawings

- SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works long shifts.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (60%)

Complete

- Civil Foundations Complete (25%)

Nov 15, 2010 (*) do not have all drawings for foundations.  We expect at least 9 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Early 2011 (*) expect at least 9 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Early 2011 (*) will issue new dates after acceptance or rejection of CO

The dates (*) will be revised as soon as the schedule review is complete, the 7EA generator and crane collision incident is unresolved.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Early 2011* expect slippage

- Unit 200 – 7FA

Early 2011

- CRITICAL AREAS OF CONCERN:

  - Building design.  Need the designer to come to site sit with Sidor and/or set up a conference call to resolve this or modifications will be done to buildings which will be back charged to the building supplier.Unresolved documents sent via FED EX have been dlivered late last week early review shown no additional info.  Howard has run an analysis.

  - The list of materials previously generated, is all material on order?

  - Send lighting BOM for order in US, prepared local PO for materials available at site, will send classified area lighting request to Sedalia.

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

- Photos

Photo 1: 7EA GSU and blast wall

Photo 2: 7EA L.O demister Module

.

Photo 3: 7EA PEECC duct bank excavation