# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 17 September, 2010, Thursday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  92 F

RANGE: 79 to 96

SITE CONDITIONS: heavy rain early (3 hrs) hot, humid afternoon

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Unfilled Mechanical/Piping (local ASAP)

Unfilled mechanical / piping expat ASAP

Mark Hanks - Electrical Supt

Jose Garcia - Elect. Field Eng.

Kyle Roskam - Civil Supt

Howard Velasquez-Civil Field Eng

Felix Martinez-QA/QC

Jason Bird - 7EA TA

Paul Olivo – Material

Unfilled T/O coordinator

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila García – Translator / Doc Control

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio

General Superintendant		0

Safety					1

Foremen				1

Electricians				0

Operators				0                     Surveyor				0

Carpenters				5

Surveyor Helper			0

Oiler Helper				0

Crane Operator			0                           Laborers				3

Truck Drivers				0

Concrete Finishers			0

Oilers					0

Plumbers				0

Iron Workers				5

Helpers

Welders				0

Total:					15

SUBCONTRACTOR PERSONNEL: ISI

General Superintendant		0

Safety					1

Foremen				1

Operators				1

Oiler Helper				0

Welders                                         5

Millwrights

Crane Operator			1                           Laborers				0

Truck Drivers				1

Mechanic	      			4

Helpers				6

Pipe fitter                                       0

Total                                             22

SUBCONTRACTOR PERSONNEL:  Coinserma

Foreman                                       2		Laborers				6

Safety                                            1		Skilled					6

Operators                                      2

Welders				2		total 19

- GENERAL ITEMS

  - Concorcio assured Site they will mobilize by Tuesday 21 Sep.  Started back fill of 7FA should finish by Saturday(Sidor asked Concorcio to work Saturday, Concorcio indicated they have commitments at “A” that prevent completion Saturday), Concorcio says will finish back fill Monday unless Sidor can bring pressure to bear.  This will delay a total of 5 days the Generator setting.

  - Received valuation #2 from Concorcio Megavatio again.  Concorcio revised valuation 2 again for 12th time, again has errors in the revised copy.

  - Dual fuel team working on 7EA.  Pipe repairs to pre fabbed spools, need QA/QC for work performed in Sedalia, no NDE reports.

  - Need to review model contract and get contractors to table to formalize contracts.

- CLIENT ISSUES/CONCERN:

  - 2.2   Access to GSU for service (grating over containment area) Chem grate manufacturer came ot site to view GSU at Site A and prepare a quote and design.

- CIVIL:

  - Concorcio agreed and surveyed the location for De-min tank, but no excavation machinery to start excavations.  Will mobilize Tuesday.

  - Discussed two week look ahead with Concorcio and have main items for planning slipping 2 days from yesterday.

  - Need to check building loading for the office and maintenance building crane loads.  Structural eng at site checked and found the building design questionable, as Sidor indicated!

  - Received drawings to prepare liquid Fuel De Scope documents.  Have stopped the work, but have not completed mark up.

  - Received Coinserma plan for the remaining work and we will review and determine if there is any reason to continue with them.  They have given plan to finish a portion will see if they follow through.

- CONCRETE FOUNDATIONS:

4.1 start excavation for de min water tank, GSU, 7FA liquid fuel module, and compressor bldg next week.

- MECHANICAL:

  - ISI with 22 people, installing 7EA Turbine and Accessory piping

  - Installed steel below 7FA turbine for inlet plenum

  - paint spec. to Sedalia for review to prepare scope and RFQ.  Received a material spec, but this requires purchase of material in US and then testing to see if it is acceptable.

  - Prepare a QA plan for tanks.  Issued scope of work for Tank PO.

- PIPING:

  - Piping installation is started, but NCR issued for materials.  Received PES QA Plan and find MTR required per plan.

  - Need a film viewer.  Will purchase US not available here, they read film with flashlight.  Have doubts to the veracity of the x-ray readings.

  - ISI started underground piping this week.  Fab spools for tie points.  Preparing ISO’s from drawings produced at site.

  - Dual fuel ongoing for 7EA.  Partial crew de mobilization next week for R&R, questioned if this will stop work.  Apparently will have no significant impact other than reduction of crew.

- ELECTRICAL:

  - Cathodic protection contractor, received quote for Tanks Monday, Sept. 6 and piping is scheduled for Friday, Sept. 10, not received at this writing.  They are reviewing the drawings against quote and preparing a list of activities to use for planning.

  - Cable schedule for hi and med voltage cables completed.  Moved list of cables to A.

  - Review and audit of electrical drawing against equipment nomenclature tags ongoing, all transformers checked will check motors and additional materials as received.

- INSTRUMENTATION AND CONTROLS:

9.    SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works two shifts or a 12 hours shift.  Need authorization to work more hours.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (60%)

Complete

- Civil Foundations Complete (25%)

Sep 15, 2010 (*) do not have all drawings for foundations.  We expect at least 7 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Dec 3, 2010 (*) expect at least 5 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Dec 11, 2010 (*) see above expect a revised schedule week end

The dates (*) will be revised as soon as the schedule review is complete and a history is trend is available.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Nov 29, 2010* expect slippage

- Unit 200 – 7FA

Dec 11, 2010

- CRITICAL AREAS OF CONCERN:

  - Commercial issues with Contractors.

  - Shortage of cement is affecting the scheduling of foundations.  We will advise when we require cement; Sidor must provide proper and adequate material.

  - Installed Site construction power, must check secondary side after stabbing fuses.  Will open after testing complete to complete installation of 208v to 480 temp power for Gen heaters and lighting CL of 7EA.  Prepaing punch list for completed works.

  - Need to assure the 7FA has all materials, contractor support, and resources from PES to meet or shorten the schedule.  Cost for GE TA is 25K per week.

  - Crane installation and acceleration of set up schedule between turbine and generator lifts for the 7FA.  Crane delay for dismantling and moving.  This will have an impact on schedule unless it starts tomorrow.  Met with 
Sidor and discussed setting Generator, if we complete back fill Saturday, they plan to lift 24 Sept.

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Substation Foundations 7FA ISO phase 7FA Generator Breaker(GA#31 7FA FG Heater | TBD |  |  |
| 7FA Fin Fan | 5 August, 10 |  |  |
| U/G piping | 5May10 | 28May10 | Prepared dwgs in field |
| Design essentially complete | 31 May | No forecast date | No forecast date |

- PICTURES:

Photo 1: 7FA crane backfill, goes to top of small protection concrete pads

Photo 2: 7EA fdn bushing ongoing

Photo 3: MH3 West duct bank pour

Photo 4: 7EA turbine fixators damage