# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 19 November, 2010, Friday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  87 F

RANGE: 74 to 93

SITE CONDITIONS: Rain, extremely hot, and humid

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Unfilled - Scheduler (A&B)

Unfilled Mechanical/Piping local ASAP

Unfilled mechanical / piping expat ASAP

Unfilled - Electrical Supt

Jose Garcia - Elect. Field Eng.

Unfilled - Civil Supt

Howard Velasquez-Civil Field Eng

Unfilled -QA/QC

unfilled - 7EA TA

Unfilled -Safety

Unfilled  – Material

MATERIAL SUPPORT:

José Angel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Unfilled -Logistics (Local)

Paola Gómez – Administration (Local)

Patricia Muños – Administration (Local)

Skeila García – Translator / Doc Control

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio – Civil Contractor

General Superintendant		1

Safety					1

Foremen				2

Supervisors				4

Electricians				1

Operators				3                   Surveyor				1

Carpenters				12

Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                          Laborers				1

Truck Drivers				1

Concrete Finishers			7

Oilers					0

Plumbers				1

Iron Workers				2

Helpers				8

Welders				1

Admin Support                               7

Total:					54

SUBCONTRACTOR PERSONNEL: ISI – Mechanical Contractor

Total                                              0

- GENERAL ITEMS

  - Concorcio started demobilization, moved equipment to staging area.

  - Poured 7EA L.O. demister and fuel gas modul foundations.

  - Received pipe not sandblasted and primed, will have ISI prepare a quote for moving the pipe, sandblasting and priming the pipe.  Will back charge purchasing.

  - GE reviewed generator damage and issued response GE wants to remove fan housing and check frame for cracks.  Will need to remobilize crew and GE TA after NDE of bolts, Presently no schedule to remobilize GE, no mechanical contractor expected next week

  - Need status of delivery for de mineralized and raw water tank materials, and cathodic protection materials purchased by Sedalia. We are expecting a response tomorrow. Material not available, now awaiting Cathodic protection and tank material to start tank erection

- CLIENT ISSUES/CONCERN:

  - Building design for office maintenance building apparently has structural design issues. Received FED EX package finally from Valencia.  We reviewed the material and find it insufficient.  Howard has created a report without blame but, showing where the assumptions are not realistic.  I suggest we turn it over to Sidor and allow them to decide.

  - Site progress and continued progress

- CIVIL:

  - Concorcio has indicated their intention to de-mob for lack of money

  - Poured last available foundations (L.O. demister and fuel gas module for 7EA) today, Concorcio indicated they will have a small crew next week to strip forms and move them to staging area.

- CONCRETE FOUNDATIONS:

  - We will collect cost for CO for additional QA/QC cost to oversee batch plants (due to Felix Martinez being away and past history with concrete here) for Compressor foundation.

- MECHANICAL:

  - Still no final report from Venefilter on flushing 7EA.  I told Venefilter’s supervisor I will not sign their invoice to release for payment without final report.

  - Foundations ready to erect tanks, awaiting material delivery.  The material delivery for Cathodic and tank material is still an issue.

- PIPING:

  - No work

- ELECTRICAL:

  - Need to return cables taken from B for use at A started doing an inventory of surplus cables from A

  - Moved MCCs to area to open and inspect and verify the delivered equipment meets the drawing and specifications.  PO prepared for issue

  - Need remaining cathodic protection equipment.  Did not arrive with last shipment!

- INSTRUMENTATION AND CONTROLS:

8.1 Need cathodic panels and dwgs.

8.2 Jose checking major electrical material against drawings

- SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works long shifts.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (60%)

Complete

- Civil Foundations Complete (25%)

Nov 15, 2010 (*) do not have all drawings for foundations.  We expect at least 9 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Early 2011 (*) expect at least 9 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Early 2011 (*) will issue new dates after acceptance or rejection of CO

The dates (*) will be revised as soon as the schedule review is complete, the 7EA generator and crane collision incident is unresolved.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Early 2011* expect slippage

- Unit 200 – 7FA

Early 2011

- CRITICAL AREAS OF CONCERN:

  - Building design.  Need the designer to come to site sit with Sidor and/or set up a conference call to resolve this or modifications will be done to buildings which will be back charged to the building supplier. Howard has run an analysis.  We do not agree with the assumptions and the calculations are incomplete.

  - The list of materials previously generated, is all material on order?

  - Send lighting BOM for order in US, prepared local PO for materials available at site, will send classified area lighting request to Sedalia. Hold

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

- Photos

Photo 1: 7EA GSU curing

Photo 2: 7EA fuel gas module fdn

Photo 3: 7EA L.O. de-mister

Photo 4: Site clean up

Photo 5: Site Clean up

Photo 6: Concorcio staging equipment for de-mob