# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 19 October, 2010, Tuesday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  92 F

RANGE: 76 to 96

SITE CONDITIONS: overcast, hot, humid,

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Unfilled  - Scheduler (A&B)

Unfilled Mechanical/Piping (local ASAP)

Unfilled mechanical / piping expat ASAP

Mark Hanks - Electrical Supt (R&R)

Jose Garcia - Elect. Field Eng.

Kyle Roskam - Civil Supt  (R&R)

Howard Velasquez-Civil Field Eng

Felix Martinez-QA/QC (R&R)

Jason Bird - 7EA TA

Dennis Maloney-Safety (R&R)

Paul Olivo – Material (R&R)

Lacy Frazier-EDGI (R&R)

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila García – Translator / Doc Control

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio – Civil Contractor

General Superintendant		1

Safety					1

Foremen				3

Supervisors				2

Electricians				0

Operators				7                    Surveyor				1

Carpenters				9

Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				3

Truck Drivers				0

Concrete Finishers			8

Oilers					0

Plumbers				0

Iron Workers				3

Helpers				 0

Welders				1

Admin Support                               9

Total:					50

SUBCONTRACTOR PERSONNEL: ISI – Mechanical Contractor

General Superintendant		1

Safety					1

Foremen				3

Operators				1

Oiler Helper				0

Welders                                        6

Millwrights			   	0

Crane Operator			1                           Laborers				0

Truck Drivers				1

Mechanic	      			7

Helpers				1

Pipe fitter                                       4

Total                                             26

- GENERAL ITEMS

  - GE TA as well as PES personnel reviewed generator damage and issue initial report to GE main office. Waiting for GE formal response. Also, GE may send GE generator specialist to check the reference generator.

  - Need to review model contract and get contractors to table to formalize contracts.  We are preparing a line item scope of work for ISI, Concorcio Megavatio, and Sialca, mechanical, civil and electrical contractors respectively. Cole and Bill working on this

  - Need status of delivery for de mineralized and raw water tank materials, and Cathodic protection materials purchased by Sedalia. We are expecting a response tomorrow. Unresolved

  - Sidor to produce floor plan for office area for Admin Bldg by Oct. 15 unresolved

  - Crane dismantled and out of 7FA area but still on site backfill removal started . Ongoing

- CLIENT ISSUES/CONCERN:

  - Building design for office maintenance building apparently has structural design issues. Communication generated to EDGI. Prepared a list of questions presented today.   Unresolved

- CIVIL:

  - Removing excess spoils from high voltage switchyard area to offsite Need issue PO!

  - Removing crane pad, separating select material from sand

  - Need issue PO for GSU 100 and Compressor Fdn for lack of contract

- CONCRETE FOUNDATIONS:

  - Forms for Compressor Foundation ongoing

  - Lean concrete placed for #100 GSU foundation, conduits and forms start Oct.18

  - Demin Water Tank. Concrete Poured.

- MECHANICAL:

  - Prepare a QA plan for tanks.  Issued scope of work for Tank PO. QA/QC plan received first draft, returned with comments. Will complete by Oct. 19

Cole and Felix reviewing expect complete this week

  - Unit 100 exhaust Stack, installing insulation and splice plates, should complete by Oct. 20

  - Dual Fuel continues liquid fuel and cooling water piping for Unit 100, will have no work by end of week, need nozzles expected ~1 Nov

  - Working lower section of 7FA Exhaust Stack, Ongoing

  - Erecting structure for 7FA Diffuser, Ongoing

  - Started  7EA oil flush ongoing

- PIPING:

  - ISI continued underground piping this week.  Fabbing spools for tie points.  Preparing ISO’s from drawings produced at site. Ongoing

  - Reducing number of workers at site next week.

- ELECTRICAL:

  - Reviewing drawings, Ongoing

  - Installing Power Panels for construction, Ongoing

  - Moved MCCs to area to open and inspect and verify the delivered equipment meets the drawing and specifications.  Ongoing

  - Need remaining Cathodic protection equipment.

- INSTRUMENTATION AND CONTROLS:

8.1 Need Cathodic panels and dwgs.

9.    SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works two shifts or a 12 hours shift.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (60%)

Complete

- Civil Foundations Complete (25%)

Nov 15, 2010 (*) do not have all drawings for foundations.  We expect at least 7 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Early 2011 (*) expect at least 7 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Early 2011 (*) will issue new dates after acceptance or rejection of CO

The dates (*) will be revised as soon as the schedule review is complete, the 7EA generator and crane collision incident is resolved.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Early  2011* expect slippage

- Unit 200 – 7FA

Early  2011

- CRITICAL AREAS OF CONCERN:

  - Crane move for 7FA generator This will be a total of four  week delay with associated cost exceeding $100K

  - Building design.  Three engineers have reviewed building design, is not suitable.  Need the designer to come to site sit with Sidor and/or set up a conference call to resolve this or modifications will be done to buildings which will be back charged to the building supplier. We are in the process of issuing a communication with suggested solutions to the design problems for the admin and warehouse building shortly..Unresolved

  - Need to assure the 7FA has all materials, contractor support, and resources from PES to meet or shorten the schedule.  Cost for GE TA is 25K per week.  GE requires more pictures and comments to GE main office for review and recommended actions. Ongoing

  - Moved 7FA Generator to free A/Bs, topographer verified location after incident to compare to original location. Waiting for documentation

  - Need to PO for NDE examination of anchor bolts for 7FA generator.

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Substation Foundations 7FA ISO phase 7FA Generator Breaker(GA#31 7FA FG Heater | TBD |  |  |

11. Pictures

Raw Water Tank Pedestal Poured

Compressors slab Forms and Rebars

Compacted material and sand of crane pad

removed from 7FA Foundation

Acc Module and LF foundations ready to start slab and walls

GSU 100 mud mat excavation for emb conduits

7FA Turbine Exhaust Difuser Set in place

Steel Frames for Exhaust in place and leveled

7EA oil flushing