# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 22 September, 2010, Wednesday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  92 F

RANGE: 78 to 94

SITE CONDITIONS: showers early hot, humid afternoon

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Unfilled Mechanical/Piping (local ASAP)

Unfilled mechanical / piping expat ASAP

Mark Hanks - Electrical Supt

Jose Garcia - Elect. Field Eng.

Kyle Roskam - Civil Supt

Howard Velasquez-Civil Field Eng

Felix Martinez-QA/QC

Jason Bird - 7EA TA

Paul Olivo – Material r&r

Unfilled T/O coordinator

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila García – Translator / Doc Control

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio

General Superintendant		0

Safety					1

Foremen				1

Electricians				0

Operators				0                     Surveyor				0

Carpenters				5

Surveyor Helper			0

Oiler Helper				0

Crane Operator			0                           Laborers				3

Truck Drivers				0

Concrete Finishers			0

Oilers					0

Plumbers				0

Iron Workers				5

Helpers

Welders				0

Total:					15

SUBCONTRACTOR PERSONNEL: ISI

General Superintendant		0

Safety					1

Foremen				1

Operators				1

Oiler Helper				0

Welders                                         6

Millwrights

Crane Operator			1                           Laborers				0

Truck Drivers				1

Mechanic	      			4

Helpers				6

Pipe fitter                                       6

Total                                             32

SUBCONTRACTOR PERSONNEL:  Coinserma

Foreman                                       2		Laborers				6

Safety                                            1		Skilled					6

Operators                                      2

Welders				2		total 19

SUBCONTRACTOR PERSONNEL:  Ceimus

Mods to containers lay down yard for office / storage

Foreman				1

Mechanic				2

Helper					2

- GENERAL ITEMS

  - Prepared milestone schedule unconstrained to show new end dates.

  - Making arrangements to de-mob expats for R & R.

  - Concorcio finished back fill for crane.

  - Crane set up will delay at least 9 days as of today, for the Generator setting.  Started crane erection today.

  - Concorcio site manager sent people and we resolved valuation #2.  PO being prepared for factura.

  - Dual fuel team working on 7EA.  Pipe repairs to pre fabbed spools, need QA/QC for work performed in Sedalia, no NDE reports.

  - Need to review model contract and get contractors to table to formalize contracts.  Spoke with Concorcio about meeting no response today.

  - Advised Coinserma to finish what can be finished this week and prepare a valuation so we can approve and de-mob them.

- CLIENT ISSUES/CONCERN:

  - Access to GSU for service (grating over containment area) Chem. grate manufacturer came to site to view GSU at Site A and prepare a quote and design.

  - Metal building design and crane loads for maintenance building.  Howard running calcs.  RFI 0010 issued.

- CIVIL:

  - Concorcio started De-min tank excavation.  Plan to pour mud mat Fri.

  - Concorcio started liquid fuel and accy module excavation.  Conduit bust will resolve AM tomorrow

  - Waste tank to poured

  - Received drawings to prepare liquid Fuel De Scope documents.  Have stopped the work, but have not completed mark up.

- CONCRETE FOUNDATIONS:

4.1 Started excavation for de min water tank, GSU, 7FA liquid fuel module, and compressor bldg next week.

4.2 Waste tank poured.

- MECHANICAL:

  - ISI with 32 people, installing 7EA Turbine and Accessory piping

  - Start LO prep for flush

  - Paint spec. to Sedalia for review to prepare scope and RFQ.  Received a material spec, but this requires purchase of material in US and then testing to see if it is acceptable.

  - Prepare a QA plan for tanks.  Issued scope of work for Tank PO.

  - Advised GE we will de-mob after generator is set onto foundation probably Friday best case.

- PIPING:

  - Piping installation is started, but NCR issued for materials.  Received PES QA Plan and find MTR required per plan.

  - Need a film viewer.  Will purchase US not available here, they read film with flashlight.  Have doubts to the veracity of the x-ray readings.

  - ISI started underground piping this week.  Fab spools for tie points.  Preparing ISO’s from drawings produced at site.

  - Dual fuel ongoing for 7EA.  Partial crew de mobilization this week for R&R.

  - Received lube oil flush quote issued PO. Collecting gaskets and plan to move cross over piping to start installation.

- ELECTRICAL:

  - Cathodic protection contractor, received quote for Tanks Monday, Sept. 6 and piping is scheduled for today, 18 Sept., received quotation this morning.

  - Cable schedule for hi and med voltage cables completed.  Moved list of cables to A.  Populate Bill Lugo spread sheet of all cables.

  - Review and audit of electrical drawing against equipment nomenclature tags ongoing, all transformers checked will check motors and additional materials as received.

  - Will prepare a scope of work for electrical contract with local contractor

  - Need weather protected space to open MCC and check internal wiring to buckets and control.

- INSTRUMENTATION AND CONTROLS:

9.    SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works two shifts or a 12 hours shift.  Need authorization to work more hours.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (60%)

Complete

- Civil Foundations Complete (25%)

Sep 15, 2010 (*) do not have all drawings for foundations.  We expect at least 7 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Dec 3, 2010 (*) expect at least 5 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Dec 11, 2010 (*) see above expect a revised schedule week end

The dates (*) will be revised as soon as the schedule review is complete and a history is trend is available.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Nov 29, 2010* expect slippage

- Unit 200 – 7FA

Dec 11, 2010

- CRITICAL AREAS OF CONCERN:

  - Commercial issues with Contractors.

  - Crane set up for 7FA generator will plan to de-mob GE TA.  This will be a total of two week delay with associated cost exceeding 50K

  - Shortage of cement is affecting the scheduling of foundations.  We will advise when we require cement; Sidor must provide proper and adequate material.   Delivered 3 week look ahead of concrete requirements.

  - Installed Site construction power, must check secondary side after stabbing fuses.  Will test today to complete installation of 208v to 480 temp power for Gen heaters and lighting CL of 7EA.  Prepared punch list for works.

  - Need to assure the 7FA has all materials, contractor support, and resources from PES to meet or shorten the schedule.  Cost for GE TA is 25K per week.  Plan to de-mob GE after setting Generator.  Earliest is now Thurs, but Friday is more realistic if soils compaction test are good.

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Substation Foundations 7FA ISO phase 7FA Generator Breaker(GA#31 7FA FG Heater | TBD |  |  |
| 7FA Fin Fan Fdn | 5 August, 10 |  |  |
| U/G piping | 5May10 | 28May10 | Prepared dwgs in field |
| Design essentially complete | 31 May | No forecast date | No forecast date |

- PICTURES:

Photo 1: duct bank backfill prep for de-mob

Photo 2: Demin backfill mud mat Friday

Photo 3: 7FA crane erection started

Photo 4: Waste tank ready for concrete