# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 22 October, 2010, Friday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  80 F

RANGE: 72 to 95

SITE CONDITIONS: nice day, mild,

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Unfilled  - Scheduler (A&B)

Unfilled Mechanical/Piping (local ASAP)

Unfilled mechanical / piping expat ASAP

Mark Hanks - Electrical Supt (R&R)

Jose Garcia - Elect. Field Eng.

Kyle Roskam - Civil Supt  (R&R)

Howard Velasquez-Civil Field Eng

Felix Martinez-QA/QC (R&R)

Jason Bird - 7EA TA

Dennis Maloney-Safety (R&R)

Paul Olivo – Material (R&R)

Lacy Frazier-EDGI (R&R)

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila García – Translator / Doc Control

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio – Civil Contractor

General Superintendant		1

Safety					1

Foremen				3

Supervisors				2

Electricians				0

Operators				4                    Surveyor				1

Carpenters				9

Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				3

Truck Drivers				0

Concrete Finishers			8

Oilers					0

Plumbers				0

Iron Workers				3

Helpers				 0

Welders				1

Admin Support                               9

Total:					47

SUBCONTRACTOR PERSONNEL: ISI – Mechanical Contractor

General Superintendant		1

Safety					1

Foremen				3

Operators				1

Oiler Helper				0

Welders                                        6

Millwrights			   	0

Crane Operator			1                           Laborers				0

Truck Drivers				1

Mechanic	      			7

Helpers				1

Pipe fitter                                       4

Total                                             26

- GENERAL ITEMS

  - GE TA as well as PES personnel reviewed generator damage and issue initial report to GE main office. Waiting for GE formal response.

  - Met with Mechanical and Electrical contractors regarding scope of work and contract.

  - Need status of delivery for de mineralized and raw water tank materials, and Cathodic protection materials purchased by Sedalia. We are expecting a response tomorrow. Material not available, now awaiting Cathodic protection and tank material to start tank erection

  - Sidor to produce floor plan for office area for Admin Bldg by Oct. 15 unresolved Sidor advises available Monday

- CLIENT ISSUES/CONCERN:

  - Building design for office maintenance building apparently has structural design issues. Communication generated to EDGI. Prepared a list of questions presented same.   Unresolved

- CIVIL:

  - Removed excess spoils from high voltage switchyard area to offsite PO prepared

  - Concorcio advises they will accept a letter directing work for GSU 100 and Compressor Fdn, will include this work into contract.  Still awaiting unit process for contract from Concorcio.

- CONCRETE FOUNDATIONS:

  - Rebar for Compressor Foundation Planned pour Wed.27 Oct

  - 100 GSU foundation, forms and rebar being prepared

  - Shot topographic points on generator and turbine couplings.  Appears that the Bench Mark was disturbed.  Will prepare a study and take corrective action Monday.  May have to purchase coupling nuts and extend anchor bolts for Silencer and exhaust 7FA

  - Permanent Survey Bench Mark on 7FA Foundation to prevent stand alone bench marks being disturbed. Ongoing.

- MECHANICAL:

  - Dual Fuel continues liquid fuel and cooling water piping for Unit 100, will have no work by end of week, need nozzles expected ~1 Nov

  - Installed lower section of 7FA Exhaust Stack and verified anchor bolt pattern, lifted after to facilitate welding to start 1 Nov.

  - Erecting structure for 7FA exhaust, bust in elevation

  - Started 7EA oil flush ongoing Problems!  Regroup and limit flushing circuits.  Pumps do not have enough flow to provide adequate flow to all circuits simultaneously.  Met with contractor and advise them to read their own procedure and comply.

- PIPING:

  - ISI to halt piping effort and concentrate on cleaning 7FA piping and covering same.  Next week they will restore piping after oil flush concludes.

  - Reducing number of workers at site next week.

- ELECTRICAL:

  - Reviewing drawings, Ongoing  Cable take off concluded and delivered to purchasing at Sedalia.

  - Need to return cables taken from B for use at A

  - Moved MCCs to area to open and inspect and verify the delivered equipment meets the drawing and specifications.  Ongoing

  - Need remaining Cathodic protection equipment.

- INSTRUMENTATION AND CONTROLS:

8.1 Need Cathodic panels and dwgs.

9.    SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works long shifts.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (60%)

Complete

- Civil Foundations Complete (25%)

Nov 15, 2010 (*) do not have all drawings for foundations.  We expect at least 9 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Early 2011 (*) expect at least 9 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Early 2011 (*) will issue new dates after acceptance or rejection of CO

The dates (*) will be revised as soon as the schedule review is complete, the 7EA generator and crane collision incident is unresolved.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Early  2011* expect slippage

- Unit 200 – 7FA

Early  2011

- CRITICAL AREAS OF CONCERN:

  - Crane move for 7FA generator This will be a total of four  week delay with associated cost exceeding $100K

  - Building design.  Three engineers have reviewed building design, is not suitable.  Need the designer to come to site sit with Sidor and/or set up a conference call to resolve this or modifications will be done to buildings which will be back charged to the building supplier. We are in the process of issuing a communication with suggested solutions to the design problems for the admin and warehouse building shortly..Unresolved

  - GE required more pictures with comments in GE main office for review and recommended actions.  Delivered photos no comments received. Ongoing

  - Moved 7FA Generator to free A/Bs, topographer verified location after incident to compare to original location. Documentation received, PO for NDE examination of anchor bolts for 7FA generator prepared

  - Made draft Change Order for damage to 7FA gen. including lifting Generator with hydraulic jacks to NDE anchor bolts.

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Substation Foundations 7FA ISO phase 7FA Generator Breaker(GA#31 7FA FG Heater | TBD |  |  |

11. Pictures

Photo 1:  7FA Generator lower exhaust

Photo 2:  Raw water tank fdn backfill complete ready for Cathodic protection, compressor first pour in background

Photo 3: De-min water tank near ready for Cathodic protection

Photo 4: 7FA stack lower section lifted after checking anchor bolt pattern

Ready to start welding 1Nov