# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 25 October, 2010, Monday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  94 F

RANGE: 76 to 96

SITE CONDITIONS: overcast, hot, humid,

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Unfilled  - Scheduler (A&B)

Unfilled Mechanical/Piping (local ASAP)

Unfilled mechanical / piping expat ASAP

Mark Hanks - Electrical Supt (R&R)

Jose Garcia - Elect. Field Eng.

Kyle Roskam - Civil Supt  (R&R)

Howard Velasquez-Civil Field Eng

Felix Martinez-QA/QC (R&R)

Jason Bird - 7EA TA

Dennis Maloney-Safety (R&R)

Paul Olivo – Material (R&R)

Lacy Frazier-EDGI (R&R)

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila García – Translator / Doc Control

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio – Civil Contractor

General Superintendant		1

Safety					1

Foremen				2

Supervisors				2

Electricians				1

Operators				1                    Surveyor				1

Carpenters				4

Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				2

Truck Drivers				4

Concrete Finishers			6

Oilers					1

Plumbers				0

Iron Workers				3

Helpers				 0

Welders				1

Admin Support                               9

Total:					41

SUBCONTRACTOR PERSONNEL: ISI – Mechanical Contractor

General Superintendant		1 Foremen				1

Safety					1

Oiler Helper				0 Welders                                        0

Millwrights			   	0 Crane Operator			0

Laborers

Truck Drivers				1

Mechanic	      			0 Helpers				0

Pipe fitter                                       6

Operators				1

Total                                             26

- GENERAL ITEMS

  - GE TA as well as PES personnel reviewed generator damage and issue initial report to GE main office. Waiting for GE formal response.

  - Met with Mechanical and Electrical contractors regarding scope of work and contract.  Received quote from Concorcio Megavatio

  - Need status of delivery for de mineralized and raw water tank materials, and Cathodic protection materials purchased by Sedalia. We are expecting a response tomorrow. Material not available, now awaiting Cathodic protection and tank material to start tank erection

  - Sidor to produce floor plan for office area for Admin Bldg by Oct. 15 unresolved Sidor advises available Monday

- CLIENT ISSUES/CONCERN:

  - Building design for office maintenance building apparently has structural design issues. Communication generated to EDGI. Prepared a list of questions presented same.   Unresolved

- CIVIL:

  - Concorcio advises they will accept a letter directing work for GSU 100 and Compressor Fdn, will include this work into contract.  Still awaiting unit process for contract from Concorcio.

- CONCRETE FOUNDATIONS:

  - Rebar for Compressor Foundation Planned pour Wed.27 Oct

  - 100 GSU foundation, forms and rebar being prepared

  - Shot topographic points on generator and turbine couplings.  Appears that the Bench Mark was disturbed.  Will prepare a study and take corrective action Monday.  May have to purchase coupling nuts and extend anchor bolts for Silencer and exhaust 7FA

  - Permanent Survey Bench Mark on 7FA Foundation to prevent stand alone bench marks being disturbed. Ongoing.

- MECHANICAL:

  - Dual Fuel has de mobilized on Site B

  - Installed lower section of 7FA Exhaust Stack and verified anchor bolt pattern, lifted after to facilitate welding to start 1 Nov.

  - Started 7EA oil flush ongoing Problems!  Regroup and limit flushing circuits.  Pumps do not have enough flow to provide adequate flow to all circuits simultaneously.  Met with contractor and advise them to read their own procedure and comply.

  - Clean and protect piping for 7FA.

- PIPING:

  - ISI to halt piping effort and concentrate on cleaning 7FA piping and covering same.  Next week they will restore piping after oil flush concludes.

  - Reduced number of workers at site.

- ELECTRICAL:

  - Reviewing drawings, Ongoing  Cable take off concluded and delivered to purchasing at Sedalia.

  - Need to return cables taken from B for use at A

  - Moved MCCs to area to open and inspect and verify the delivered equipment meets the drawing and specifications.  Ongoing

  - Need remaining Cathodic protection equipment.

- INSTRUMENTATION AND CONTROLS:

8.1 Need Cathodic panels and dwgs.

9.    SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works long shifts.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (60%)

Complete

- Civil Foundations Complete (25%)

Nov 15, 2010 (*) do not have all drawings for foundations.  We expect at least 9 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Early 2011 (*) expect at least 9 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Early 2011 (*) will issue new dates after acceptance or rejection of CO

The dates (*) will be revised as soon as the schedule review is complete, the 7EA generator and crane collision incident is unresolved.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Early  2011* expect slippage

- Unit 200 – 7FA

Early  2011

- CRITICAL AREAS OF CONCERN:

  - Crane move for 7FA generator This will be a total of four  week delay with associated cost exceeding $100K  Prepare Change order and CO for Damages to 7FA generator

  - Building design.  Three engineers have reviewed building design, is not suitable.  Need the designer to come to site sit with Sidor and/or set up a conference call to resolve this or modifications will be done to buildings which will be back charged to the building supplier. We are in the process of issuing a communication with suggested solutions to the design problems for the admin and warehouse building shortly..Unresolved

  - GE required more pictures with comments in GE main office for review and recommended actions.  Delivered photos no comments received. Ongoing

  - Moved 7FA Generator to free A/Bs, topographer verified location after incident to compare to original location. Documentation received, PO for NDE examination of anchor bolts for 7FA generator prepared.

  - Made draft Change Order for damage to 7FA gen. including lifting Generator with hydraulic jacks to NDE anchor bolts.

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Substation Foundations 7FA ISO phase 7FA Generator Breaker(GA#31 7FA FG Heater | TBD |  |  |

11. Pictures

Photo 1:  GSU 100 Rigid conduits embedded

Photo 2:  Compressors Anchor Bolts

Photo 3: Raw water tank ring and central pedestal ready for Cathodic Protection

Photo 4: De-min tank ring wall ready for Cathodic Protection