# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 27 September, 2010, Monday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  82 F

RANGE: 76 to 95

SITE CONDITIONS: overcast, hot, humid

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Unfilled Mechanical/Piping (local ASAP)

Unfilled mechanical / piping expat ASAP

Mark Hanks - Electrical Supt

Jose Garcia - Elect. Field Eng.

Kyle Roskam - Civil Supt

Howard Velasquez-Civil Field Eng

Felix Martinez-QA/QC

Jason Bird - 7EA TA

Paul Olivo – Material r&r

Unfilled T/O coordinator

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila García – Translator / Doc Control

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio

General Superintendant		0

Safety					1

Foremen				1

Electricians				0

Operators				0                     Surveyor				0

Carpenters				5

Surveyor Helper			0

Oiler Helper				0

Crane Operator			0                           Laborers				3

Truck Drivers				0

Concrete Finishers			0

Oilers					0

Plumbers				0

Iron Workers				5

Helpers

Welders				0

Total:					15

SUBCONTRACTOR PERSONNEL: ISI

General Superintendant		0

Safety					1

Foremen				1

Operators				1

Oiler Helper				0

Welders                                         6

Millwrights

Moved to Site A today

Crane Operator			1                           Laborers				0

Truck Drivers				1

Mechanic	      			4

Helpers				6

Pipe fitter                                       6

Total                                             32

SUBCONTRACTOR PERSONNEL:  Coinserma de-mobing

Foreman                                       2		Laborers				6

Safety                                            1		Skilled					6

Operators                                      2

Welders				2		total 19

SUBCONTRACTOR PERSONNEL:  Ceimus punch list today

Mods to containers lay down yard for office / storage

Foreman				1

Mechanic				2

Helper					2

- GENERAL ITEMS

  - Crane set up will delay at least 12 days as of today.  We are informed the crane people have issue with Sidor and will be ready to set Generator Wed or Thurs .  Crane erection not progressing today.

  - Dual fuel team working on 7EA.  Pipe repairs to pre fabbed spools, need QA/QC for work performed in Sedalia, no NDE reports.

  - Need to review model contract and get contractors to table to formalize contracts.  Spoke with Concorcio about meeting no response today.

  - Coinserma came to site to advise they have a Union problem and must finish the week.  I reviewed with Bill Lugo and we can have them finish the works left unfinished if they do not overrun present PO or extend past Saturday.

  - Need status of delivery for de min and raw water tank materials

- CLIENT ISSUES/CONCERN:

  - Access to GSU for service (grating over containment area) Chem. grate manufacturer came to site to view GSU at Site A and prepare a quote and design.

  - Metal building design and crane loads for maintenance building.  Howard calculated loads and has advised we have a fdn problem, need the O/H crane loads to prepare a solution.  RFI 0010 issued.

- CIVIL:

  - Concorcio finished De-min tank excavation and poured mud mat, installing forms today.

  - Concorcio finished liquid fuel and accy module excavation and backfill, their U/G electricians will extend spare conduits.

  - Received drawings to prepare liquid Fuel De Scope documents.  Have stopped the work, but have not completed mark up, prepared the material takeoff, will review again and issue ASAP.

  - Need anchor bolts contacted Maracaibo for vendor names.  High priority

- CONCRETE FOUNDATIONS:

  - Started excavation for raw water tank and compressor bldg will delay compressor for lack of bolts and start GSU

  - Poured second pour waste tanks.

  - Need to extend spare conduits on 7FA for accy module and liq fuel modules foundations

- MECHANICAL:

  - ISI with few workers after elections.

  - Started LO prep for flush, moving materials from A.  Ongoing

  - Paint spec. to Sedalia for review to prepare scope and RFQ.  Received a material spec, but this requires purchase of material in US and then testing to see if it is acceptable.

  - Prepare a QA plan for tanks.  Issued scope of work for Tank PO.

  - Advised GE to return tomorrow to set gen onto foundation.

- PIPING:

  - Piping installation is started, but NCR issued for materials.  Received PES QA Plan and find MTR required per plan.

  - Need a film viewer.  Will purchase US not available here, they read film with flashlight.  Have doubts to the veracity of the x-ray readings.

  - ISI started underground piping this week.  Fab spools for tie points.  Preparing ISO’s from drawings produced at site.

  - Dual fuel ongoing for 7EA.  Partial crew de mobilization this week for R&R.

- ELECTRICAL:

  - Cathodic protection contractor, received quote for Tanks Monday, Sept. 6 and piping is scheduled for today, 18 Sept., received quotation they will come to site tomorrow and discuss the planned installation after testing conductivity in A.

  - Cable schedule for hi and med voltage cables completed.  We are awaiting EDGI cable list to determine if we have missed anything.

  - Review and audit of electrical drawing against equipment nomenclature tags ongoing, all transformers checked will check motors and additional materials as received.

  - Preparing a scope of work for electrical contract with local contractor

  - Need weather protected space to open MCC and check internal wiring to buckets and control.

  - Need to prepare a CO for delays in energizing temp const power to site.  De mob of equipment to Site A, shut down const power at site.  Met with Sidor late afternoon to jointly conduct punch list for energizing.

- INSTRUMENTATION AND CONTROLS:

9.    SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works two shifts or a 12 hours shift.  Need authorization to work more hours.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (60%)

Complete

- Civil Foundations Complete (25%)

Sep 15, 2010 (*) do not have all drawings for foundations.  We expect at least 7 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Dec 3, 2010 (*) expect at least 5 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Dec 11, 2010 (*) see above expect a revised schedule week end

The dates (*) will be revised as soon as the schedule review is complete and a history is trend is available.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Early  2011* expect slippage

- Unit 200 – 7FA

Early  2011

- CRITICAL AREAS OF CONCERN:

  - Commercial issues with Contractors.

  - Crane set up for 7FA generator will plan to de-mob GE TA after setting gen.  This will be a total of three week delay with associated cost exceeding 50K

  - Shortage of cement is affecting the scheduling of foundations.  We have advised when we require cement; Sidor must provide proper cement and adequate other material (sand and gravel).

  - Installed Site construction power, must check secondary side after stabbing fuses.  Will test tomorrow after installing another ground rod.  Prepared punch list for works with Sidor.  Lack of generators and light plants are now a cost to Sidor, they are not accepting temp power even though they inspected prior to shut down to connect.

  - Need to assure the 7FA has all materials, contractor support, and resources from PES to meet or shorten the schedule.  Cost for GE TA is 25K per week.  Plan to de-mob GE after setting Generator.  Earliest is now Tuesday but Wednesday is more realistic if crane erection completed Tuesday

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Substation Foundations 7FA ISO phase 7FA Generator Breaker(GA#31 7FA FG Heater | TBD |  |  |
| 7FA Fin Fan Fdn | 5 August, 10 |  |  |
| U/G piping | 5May10 | 28May10 | Prepared dwgs in field |
| Design essentially complete | 31 May | No forecast date | No forecast date |

- PICTURES:

Photo 1: de min tank forms

Photo 2: compressor fdn excavation

Photo 3: raw water exc and backfill

Photo 4: 7FA gen crane status and liquid fuel / accy excavations