# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 28 October, 2010, Thursday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  94 F

RANGE: 76 to 96

SITE CONDITIONS: overcast, rain

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Unfilled  - Scheduler (A&B)

Unfilled Mechanical/Piping local ASAP

Unfilled mechanical / piping expat ASAP

Mark Hanks - Electrical Supt (R&R)

Jose Garcia - Elect. Field Eng.

Kyle Roskam - Civil Supt (R&R)

Howard Velasquez-Civil Field Eng

Felix Martinez-QA/QC (R&R)

Jason Bird - 7EA TA

Dennis Maloney-Safety (R&R)

Paul Olivo – Material (R&R)

Lacy Frazier-EDGI (R&R)

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila García – Translator / Doc Control

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio – Civil Contractor

General Superintendant		1

Safety					1

Foremen				1

Supervisors				2

Electricians				1

Operators				4                    Surveyor				1

Carpenters				10

Surveyor Helper			2

Oiler Helper				0

Crane Operator			1                           Laborers				0

Truck Drivers				1

Concrete Finishers			6

Oilers					0

Plumbers				1

Iron Workers				3

Helpers				4

Welders				1

Admin Support                               7

Total:					47

SUBCONTRACTOR PERSONNEL: ISI – Mechanical Contractor

General Superintendant		0 		Supervisor				0.

Coordinator				1		Safety					1

Foremen				0		Operators				0

Oiler Helper				0 		Welders                                         0

Millwrights			   	0		Crane Operator			1

Laborers				0		Truck Drivers				1

Mechanic	      			0		Helpers				6

Pipe fitter                                       0		Total                                             8

- GENERAL ITEMS

  - Rain and no concrete for 7Fa accessory module.

  - GE TA as well as PES personnel reviewed generator damage and issue initial report to GE main office. Waiting for GE formal response.   Attempted to connect to GE conference call power outages made connection impossible.  Have had multiple power outages today, durations up to 3 hours.

  - Need status of delivery for de mineralized and raw water tank materials, and Cathodic protection materials purchased by Sedalia. We are expecting a response tomorrow. Material not available, now awaiting Cathodic protection and tank material to start tank erection

  - Sidor to produce floor plan for office area for Admin Bldg by Oct. 27 received CAD drawings today.

- CLIENT ISSUES/CONCERN:

  - Building design for office maintenance building apparently has structural design issues. Communication generated to EDGI. Prepared a list of questions presented same.   Unresolved

  - Oil flush is completed as of 26 Oct, no report received.

- CIVIL:

  - Concorcio advises they will accept a letter directing work for GSU 100 and Compressor Fdn, will include this work into contract.  Unit process for contract from Concorcio are delivered will review and proceed.  I am holding on the letter directing Concorcio to perform additional work (in lieu of a contract) so I will not make a long term financial commitments, that may not be possible to meet.

- CONCRETE FOUNDATIONS:

  - We will collect cost for CO for additional QA/QC cost to oversee batch plants (due to Felix  Martinez being on R&R and past history with concrete here) for Compressor foundation.

  - 100 GSU foundation, forms and rebar being prepared

  - Will pour 7FA accy module floor and walls tomorrow AM Sidor unable to provide concrete.

- MECHANICAL:

  - 7EA oil flush completed quality is very good.  Will prepare a critique of the flushing procedure results for further reference.

  - Clean and protect piping for 7FA both in lay down yard and at machine.

  - Removing materials not installed from site to lay down Yard.

  - Need to know status of the Raw and De-min water tank materials (rolled shell plates, top plates, and bottom plates.  De-min presently in fabrication, raw water to ship on next ship, expect delivery at site no earlier than 3 weeks.

- PIPING:

  - Restoring L.O. piping after oil flush and installing permanent gauges, fixtures, and gaskets.

- ELECTRICAL:

  - Reviewing drawings, preparing pulling schedule for 7EA.

  - Need to return cables taken from B for use at A

  - Moved MCCs to area to open and inspect and verify the delivered equipment meets the drawing and specifications.  Hold for electricians

  - Need remaining Cathodic protection equipment.

- INSTRUMENTATION AND CONTROLS:

8.1 Need Cathodic panels and dwgs.

8.2 Met with PES DCS people tomorrow regarding controls, need to explain to Sidor they are not getting a DCS system.

9.    SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works long shifts.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (60%)

Complete

- Civil Foundations Complete (25%)

Nov 15, 2010 (*) do not have all drawings for foundations.  We expect at least 9 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Early 2011 (*) expect at least 9 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Early 2011 (*) will issue new dates after acceptance or rejection of CO

The dates (*) will be revised as soon as the schedule review is complete, the 7EA generator and crane collision incident is unresolved.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Early  2011* expect slippage

- Unit 200 – 7FA

Early  2011

- CRITICAL AREAS OF CONCERN:

  - Building design.  Three engineers have reviewed building design, is not suitable.  Need the designer to come to site sit with Sidor and/or set up a conference call to resolve this or modifications will be done to buildings which will be back charged to the building supplier. We are in the process of issuing a communication with suggested solutions to the design problems for the admin and warehouse building shortly..Unresolved

  - GE required more pictures with comments in GE main office for review and recommended actions.  Delivered photos no comments received. Ongoing

  - Moved 7FA Generator to free A/Bs, topographer verified location after incident to compare to original location. Documentation received, PO for NDE examination of anchor bolts for 7FA generator prepared.

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Substation Foundations 7FA ISO phase 7FA Generator Breaker(GA#31 7FA FG Heater | TBD |  |  |

11. Pictures

No photos