Table of Contents

1. Executive Summary

EPC

Weekly Report 25 Sep to 1 Oct 2010Date: 2-Oct-10Project: Sidor Site B, Puerto Ordaz Venezuela Written By: Cole Franklin ProEnergy EPC Project Mgr

ProEnergy Site Manager

William Lugo

Cole Franklin

1.1 Safety and Regulatory Compliance

1.2 Personnel/Staffing

1.3 Weekly Accomplishments

1.4 Scheduling Conflicts

1.5 Site Manager Commentary and Amplifying Remarks

2. Engineering and Design

2.1 General Arrangement

2.2 Site/Civil/ Structural

2.3 Mechanical

2.4 Electrical

2.5 Instruments & Control

2.6 O&M Manuals

3. Procurement

3.1 Purchase Order Requests

3.2 Equipment & Material Quotations

3.3 Purchase Order

4. Contracts

4.1 EPC Contract

4.2 Construction Subcontracts

4.3 Proposal and Quotes

5. Construction

5.1 Schedule

5.2 Equipment Delivery Status (expediting report)

5.3 Civil

5.3.1 Site Preparation

5.3.2 Centerline Foundation

5.3.3 GSU Foundation

5.3.4 Auxiliary Foundations

5.4.1 Centerline Equipment Installation

5.4.2 Centerline Piping Installation

5.4.3 Auxiliary Piping Installation

5.4.4 Underground Piping Installation

5.4.5 Above Ground Piping Installation

5.4.6 Balance of Plant (BOP) Piping Installation

5.5 Electrical

5.5.1 Duct Bank Installation

5.5.2 Centerline Electrical Installation

5.5.3 Auxiliary Electrical Installation

5.5.4 Balance of Plant (BOP) Installation

5.6 QA/QC

5.6.1 Equipment Testing

5.6.2 Nonconformity Report

5.6.3 Drawing Revisions

5.6.4 CWI Reports

5.6.5 As-built Drawings

6 Start-Up & Commissioning

6.1 Schedule

6.2 Equipment Status

6.3 Punch list

6.4 Equipment Checkout

6.5 Equipment Functional Test

6.6 Equipment Turnover

6.7 Performance Testing

6.8 Emission Testing

7 Mobilization

7.1 Schedule

7.2 Operating Procedure Development

7.3 Operation Staff Training

7.4 Spare Parts/Inventory Status

1. Executive Summary.

This review is for the week from 25 Sept. to 1 October 2010.  The safety is relatively good, minor issues with contractors and PPE.

The Sidor backfill for the crane pad was completed and we assembled crane and set 7FA generator.  The crane disassembly has not started.  This will cause a delay until the crane and backfilled material can be removed.

Contractor quality is good, contractor commercial issues and lack of contract are causing some issues, but payment to contractor has enlivened them.

We met with Coinserma, they are moving their equipment out. I have tried to string them along until we can get a better contractor.  The duct bank delays have now caused us to by pass a portion of the work to advance the foundations that can be completed without impact by duct bank proximity.  We have reviewed their valuations and are awaiting corrections to release their payments.

The two week slow down for site b has been put off, we need materials and contracts for lack of PO’s for contractors.

We are spending a large portion of the site staff time doing engineering reviews and corrective actions that are not normally in Site team scope.  It is very frustrating to all.

1.1 Safety & Regulatory Compliance –

- General Safety will be maintained at all times on site, Concorcio is slow to respond and we will request a new site safety supervisor.  Overhead work started, and night work around open excavations for 7FA repairs.

- Daily safety audits are now in place, weekly recap to office.

- Contractor will be directed to install permanent Bulletin board will be installed.

- The safety people and contractor prepared a recap of all man-hours worked, this figure will be incorporated into the sign.

  - Personnel/Staffing –

Cole Franklin (Site Manager)

Keith McMurray (scheduler shared A&B)

Skeila Garcia (doc control and translator)

Paola Gomez (administrative assist. Local hire)

Patricia Munoz (logistics assist. Local hire)

Daniel Febres (logistics support local hire)

Ysren Gomez (safety supervisor Local hire)

Kyle Rosken (Civil Superintendant)

Mark Hawks (Electrical supervisor)

Felix Martinez (QA/QC supervisor)

Paulo Olivio (Material coordinador)

Jose Martinez (material management local hire)

Jason Byrd (TA 7EA 7FA)

Julio Daniels tool room attendant

Jose Garcia Electrical field engineer

Howard Velasquez Civil field engineer

Agustin Navarro GE on site this week, have demobilized until crane and backfill is removed.

1.3 Weekly Accomplishments

- 7FA gen set onto foundaiton

- Excavations completed for demin tank, raw water tank, and compressor fdn.  Torrential rains have caued some set back, but will progress next week after we dig out.

- Waste tank second pour poured

- Poured mud mat for de min tank and raw tank and a section of duct bank to extend out of the raw water tank backfill area.

  - Scheduling Conflicts –

- Need anchor bolts, vendor in Maracaibo advises they can ship within one week after receipt of PO.

- U/G piping contractor is again at work, they worked this week end.

- Must move on the office and maintenance bldg.  Review of the building design after questions by Sidor.  Howard has determined that we have a problem with the foundation based on crane loads.  Bill asked we develop a solution, but it is near impossible without overhead crane loads.  Sent e-mail to crane manufacturer for design loads.

1.5– Site Managers Commentary and Amplifying Remarks

The remaining duct bank adjacent to the 7EA is excavated have de-mobbed Coinserma.  Have not fired them pending quotes review from Concorcio.  Concorcio makes more sense as they control when they excavate and pour duct banks and can backfill only to depth necessary to start the adjacent foundations.

Mark and Jose (field engineer) have prepared a BOM from electrical drawings and inventoried the materials in lay down yard.  We will send the results to EDGA probably today. We are attempting to finish a line item scope of work as a precursor to a contract negotiation.  Plan to try to get an electrical contractor quoting on a contract so we can start when the cable is returned.

No site power since Friday morning, problem with incoming power to Sidor area.

Engineering and Design

2.1.1 Have no resolution on building design problems from Septagon Mesco

2.1.2 Grounding

- The grounding shown on grounding drawings is not in accordance with the discussion with Sidor, we are proceeding to ground in accordance with Sidor requiremsnt and red line drawings for future correction.  Need to put it to bed!

2.1.3 Geo tech membrane treated fuel oil tank

- The geo tech fabric for fuel oil tank arrived.   Supplier assured they will pass their guarantee to Sidor when we turned over the material to SIDOR.

  - – Site /Civil /Structural

    - Waste tank ring wall poured.

    - Poured several mud mats and a portion of duct bank where necessary to progress.

  - – Mechanical –

    - The 7EA stack weld out near complete

    - 7EA piping ongoing

2.4 – Electrical –

2.4.1   Take off completed for all identified Hi Voltage and Medium Voltage cable

2.4.2    Completed review of transformers against drawings.

2.4.3    Move MCC to secure area next week and open and compare to drawings.

2.5 – Instrumentation - To Be Completed

2.5.1 EDGI tells us the missing information is due from PES

2.6 – O&M Manuals –

2.6.1 Need to transmit officially one copy 7FA manual.  CD being delivered to Sidor

3. Procurement

3.1 – Purchase Order Requests

- Anchor bolts for hi voltage yard and buildings

- Compressor bldg and compressor bolts, RFQ sent to Miner, awaiting PO to start.

3.2 – Equipment & Material Quotations –

1.

3.3 - Purchase Order

Demin and Raw tank PO issued to same contractor as A

Awaitng more info for Cathodic protection installation services PO

4. Contract

4.1 – EPC Contract –

- CO 001 sent of Poor Soils Site B

- CO002 sent for Backfill under crane due to CO001

- CO 003 construction power distribution to site materials

- CO 004 core drilling to Derwick for Sidor provided concrete

- CO 005 issued for core drilling

- CO 006 issued for moving diesel tank

- CO 008 prepared for back fill under crane at 7FA

- CO010 for repairs to lay down road

- CO for Paint

4.2 – Construction Subcontracts –

1. Contract negotiations with Concorcio not complete, apparently they came to my office when we were setting Genrator

4.3 – Proposal & Quotes

1. Received quote from Ceimusa for office and maintenance building.	Completed the work on container modifications for warehouse office and calibration area.

2. Need quote for GE site office

3. Need quote to make the internet access work, GE requires access to drawings and we cannot currently provide adequate bandwidth to enter “PNet”.

5. Construction

5.1 – Schedule

  - Schedule two week look ahead will be issued to Sidor next week.

  - Received three week look ahead from Concorcio

  - 25 day delay for the setting of Generator for 7FA

5.2 – Equipment Delivery – in progress

5.2.1 Material issues, early delivery of packing list before receipt of material, and P.O.s are a major problem

5.3 – Mechanical –

5.3.1 7EA build continues need to pour additional foundations

5.4 – Electrical –

5.4.1 duct bank and manholes stopped except where necessary to complete the foudnations

Preparing scope for electrical contractor

5.5 QA/QC –

- Ongoing inspections concrete, formworks and anchor bolts.

- Started collecting documents for inclusion in T/O manuals

- Weld map prepared 2 production x-rays taken, need film reader to review the x-ray film.

6 Startup & Commissioning –

7 Startup Mobilization - None

Picture 1: compressor fdn

Picture 2: De min tank mud mat raw water tank exc

Picture 3: 7FA crane ready to lift

Picture 4: 7FA generator on fdn

Picture 5:  Rain aftermath

Picture 6: Rain aftermath tanks area