Table of Contents

1. Executive Summary

EPC

Weekly Report 28 to 3 Sep 2010Date: 4-Sep-10Project: Sidor Site B, Puerto Ordaz Venezuela Written By: Cole Franklin ProEnergy EPC Project Mgr

ProEnergy Site Manager

William Lugo

Cole Franklin

1.1 Safety and Regulatory Compliance

1.2 Personnel/Staffing

1.3 Weekly Accomplishments

1.4 Scheduling Conflicts

1.5 Site Manager Commentary and Amplifying Remarks

2. Engineering and Design

2.1 General Arrangement

2.2 Site/Civil/ Structural

2.3 Mechanical

2.4 Electrical

2.5 Instruments & Control

2.6 O&M Manuals

3. Procurement

3.1 Purchase Order Requests

3.2 Equipment & Material Quotations

3.3 Purchase Order

4. Contracts

4.1 EPC Contract

4.2 Construction Subcontracts

4.3 Proposal and Quotes

5. Construction

5.1 Schedule

5.2 Equipment Delivery Status (expediting report)

5.3 Civil

5.3.1 Site Preparation

5.3.2 Centerline Foundation

5.3.3 GSU Foundation

5.3.4 Auxiliary Foundations

5.4.1 Centerline Equipment Installation

5.4.2 Centerline Piping Installation

5.4.3 Auxiliary Piping Installation

5.4.4 Underground Piping Installation

5.4.5 Above Ground Piping Installation

5.4.6 Balance of Plant (BOP) Piping Installation

5.5 Electrical

5.5.1 Duct Bank Installation

5.5.2 Centerline Electrical Installation

5.5.3 Auxiliary Electrical Installation

5.5.4 Balance of Plant (BOP) Installation

5.6 QA/QC

5.6.1 Equipment Testing

5.6.2 Nonconformity Report

5.6.3 Drawing Revisions

5.6.4 CWI Reports

5.6.5 As-built Drawings

6 Start-Up & Commissioning

6.1 Schedule

6.2 Equipment Status

6.3 Punch list

6.4 Equipment Checkout

6.5 Equipment Functional Test

6.6 Equipment Turnover

6.7 Performance Testing

6.8 Emission Testing

7 Mobilization

7.1 Schedule

7.2 Operating Procedure Development

7.3 Operation Staff Training

7.4 Spare Parts/Inventory Status

1. Executive Summary.

This review is for the week from 28 August to 3 September 2010.  The safety is good, but had one incident.  A vendor vehicle backed into a parked vehicle on site.

Need to develop a means of tracking material from requisition (both local and US), purchase, shipment, and finally to site, that allows Site to know where the material is in the delivery cycle.  Will review Protrack next week with Bill.

The 7EA installation continues, installation of piping inside enclosures ongoing, stack welding ongoing final stack sections installed.  The foundation for the 7FA was completed including the repair.

Crane backfill for setting the 7FA turbine and generator completed.  Was a 5 day delay to start crane installation by Sidor that has added 4 to 5 days to turbine and generator installation.

Contractor quality is relatively good, contractor commercial issues and lack of contract are causing planning nightmares.  We advised the contractor to start staffing up, met with Concorcio to discuss this.  Hooper gave a draft contract to Concorcio, they reviewed and rejected.   We are not preparing PO for specific work and delivering.

Duct bank Civil contractor has poured manholes  and sections of duct bank, expect to utilize these large excavations by installing pipe.  Have asked for cost to have the same contractor excavate for pipe install.  Coinserma is being very conservative and may require we go to a cost plus contract or adjusted fixed fee contract.  Coinserma prepared something but have not sent it to me.

The 7FA generator pedestal and repair were poured.  The turbine installation , appears will slip.  Sidor installed crane is not complete.  Haul Road for moving the turbine / generator is not completed for 5 Sep.

1.1 Safety & Regulatory Compliance –

- General Safety will be maintained at all times on site, Concorcio is slow to respond and we will request a new site safety supervisor.  Overhead work started, and night work around open excavations for 7FA repairs.

- Daily safety audits are now in place, weekly recap to office.

- Contractor will be directed to install permanent Bulletin board will be installed.

- The safety people and contractor prepared a recap of all man-hours worked, this figure will be incorporated into the sign.

  - Personnel/Staffing –

Cole Franklin (Site Manager)

Keith McMurray (scheduler shared A&B)

Skeila Garcia (doc control and translator)

Paola Gomez (administrative assist. Local hire)

Patricia Munoz (logistics assist. Local hire)

Daniel Febres (logistics support local hire)

Ysren Gomez (safety supervisor Local hire)

Kyle Rosken (Civil Superintendant)

Mark Hawks (Electrical supervisor)

Felix Martinez (QA/QC supervisor)

Paulo Olivio (Material coordinador)

Jose Martinez (material management local hire)

Jason Byrd (TA 7FA)

Julio Daniels tool room attendant

Jose Garcia Electrical field engineer

Howard Velasquez Civil field engineer

GE on site this week

1.3 Weekly Accomplishments

- MH 3 poured and first section of duct bank

- The 7EA installation continues.

- The 7FA slab (first section) poured awaiting completion of repairs

- The 7FA turbine pedestal poured

- Excavated for duct bank between MH4 and MH3

  - Scheduling Conflicts –

- The duct bank and manholes / hand holes are critical around 7EA.  We have the field engineers preparing sketches to forward the work and are finding errors in EDGI drawings or are receiving the revised drawings after we have started the work..  Concorcio refused to start this (commercial issue) have directed Coinserma to start this section of duct bank in addition to their other work with U/G piping and duct bank.

- U/G piping is started need the piping supervisor at site

- GSU delayed for duct bank, Coinserma excavating duct bank below and adjacent to the GSU  foundation.

- U/G piping contractor is double jointing pipe, has been released this week to complete welding of 7EA stack so it can be set before Sidor de-mobilizes the crane.  Stack set for 7EA Thursday.

1.5– Site Managers Commentary and Amplifying Remarks

The duct bank contractor has progressed, but did not finish the pour of second section of duct bank.  Conduit change impacted the finish; the conduits are being added will be complete by Monday COB.  They completed the first PO scope this week except the revision to electrical dwgs.  Approved first valuation to invoice.

The rainy season has been an issue, we had delays due to rain but no days lost.  We need additional Concorcio people and machinery.  Will meet them Monday when their Site Manager is back.

Got a new electrical field engineer, he will follow the duct bank contractor in tandem with Mark and Kyle and finally will start take offs for electrical equipment and track drawings.

- Engineering and Design

2.1.1 Received the following drawings this week;

2.1.2 Grounding

- The grounding shown on grounding drawings is not in accordance with the discussion with Sidor regarding grounding of equipment.  This will become a major issue.  Need to put it to bed!

2.1.3 Geo tech membrane treated fuel oil tank

- The geo tech fabric is ordered for fuel oil tank.  Fuel tank on hold pending CO to move tank or remove it from scope.  Plan to have a meeting to resolve this next week.  We have put into Contractor Client meeting minutes we are proceeding as if this issue is resolved.

  - – Site /Civil /Structural

    - The 7FA repairs and generator pedestal completed.

    - Layout for 7FA fixators completed.

  - – Mechanical –

    - The 7EA stack erection completed

    - 7EA piping ongoing

2.4 – Electrical –

2.4.1    Duct bank contractor on site, ongoing.

2.4.2    Take off completed for all identified Hi Voltage and Medium Voltage cable

2.5 – Instrumentation - To Be Completed

2.5.1 EDGI tells us the missing information is due from PES

2.5.2 Preparing a list of all electrical electronic parts removed and sent to Termozuila

2.6 – O&M Manuals –

2.6.1 Need to transmit officially one copy 7FA manual.  Holding for ransom.

3. Procurement

3.1 – Purchase Order Requests

- New quote storage container for material storages, released

- Construction power CO for transformer installation delivered, CO issued to Derwick.  Released using down payment for container mods

- Hilti RE 500 for anchors

- Anchor bolts for hi voltage yard and buildings

3.2 – Equipment & Material Quotations –

1.

3.3 - Purchase Order

Demin and Raw tank PO issued to same contractor as A

4. Contract

4.1 – EPC Contract –

- CO 001 sent of Poor Soils Site B

- CO002 sent for Backfill under crane due to CO001

- CO 003 construction power distribution to site materials

- CO 004 core drilling to Derwick for Sidor provided concrete

- CO 005 issued for core drilling

- CO 006 issued for moving diesel tank

- CO 008 prepared for back fill under crane at 7FA

- CO010 for repairs to lay down road

- CO for Paint

4.2 – Construction Subcontracts –

1. Change Order to Coinserma

2. Contract negotiations with Concorcio

4.3 – Proposal & Quotes

5. Construction

5.1 – Schedule

  - Schedule two week look ahead will be issued to Sidor next week.  6 day delay for concrete 7FA

5.2 – Equipment Delivery – in progress

5.2.1 Material issues, early delivery of packing list before receipt of material, and P.O.s are a major problem

5.3 – Mechanical –

5.3.1 7EA build continues

5.4 – Electrical –

5.4.1 duct bank and manholes ongoing

5.5 QA/QC –

- Ongoing inspections concrete, formworks and anchor bolts.

- Started collecting documents for inclusion in T/O manuals

- Weld map prepared 2 production x-rays taken, need film reader to review the x-ray film.

6 Startup & Commissioning –

7 Startup Mobilization - None

Picture 1: 7EA Stack Second Piece Set

Picture 2: 7EA Final piece set

Picture 3: 7FA Generator pedestal poured

Picture 4: 7FA repair grouting dowells

Picture 5: 7FA Crane started move for erection

Photo 6: 7EA Duct bank near GSU