Table of Contents

1. Executive Summary

EPC

Weekly Report 31 July to 6 Aug 2010Date: 7-Aug-10Project: Sidor Site B, Puerto Ordaz Venezuela Written By: Cole Franklin ProEnergy EPC Project Mgr

ProEnergy Site Manager

William Lugo

Cole Franklin

1.1 Safety and Regulatory Compliance

1.2 Personnel/Staffing

1.3 Weekly Accomplishments

1.4 Scheduling Conflicts

1.5 Site Manager Commentary and Amplifying Remarks

2. Engineering and Design

2.1 General Arrangement

2.2 Site/Civil/ Structural

2.3 Mechanical

2.4 Electrical

2.5 Instruments & Control

2.6 O&M Manuals

3. Procurement

3.1 Purchase Order Requests

3.2 Equipment & Material Quotations

3.3 Purchase Order

4. Contracts

4.1 EPC Contract

4.2 Construction Subcontracts

4.3 Proposal and Quotes

5. Construction

5.1 Schedule

5.2 Equipment Delivery Status (expediting report)

5.3 Civil

5.3.1 Site Preparation

5.3.2 Centerline Foundation

5.3.3 GSU Foundation

5.3.4 Auxiliary Foundations

5.4.1 Centerline Equipment Installation

5.4.2 Centerline Piping Installation

5.4.3 Auxiliary Piping Installation

5.4.4 Underground Piping Installation

5.4.5 Above Ground Piping Installation

5.4.6 Balance of Plant (BOP) Piping Installation

5.5 Electrical

5.5.1 Duct Bank Installation

5.5.2 Centerline Electrical Installation

5.5.3 Auxiliary Electrical Installation

5.5.4 Balance of Plant (BOP) Installation

5.6 QA/QC

5.6.1 Equipment Testing

5.6.2 Nonconformity Report

5.6.3 Drawing Revisions

5.6.4 CWI Reports

5.6.5 As-built Drawings

6 Start-Up & Commissioning

6.1 Schedule

6.2 Equipment Status

6.3 Punch list

6.4 Equipment Checkout

6.5 Equipment Functional Test

6.6 Equipment Turnover

6.7 Performance Testing

6.8 Emission Testing

7 Mobilization

7.1 Schedule

7.2 Operating Procedure Development

7.3 Operation Staff Training

7.4 Spare Parts/Inventory Status

1. Executive Summary.

This review is for the week from 31 July to 6 August 2010.  Concorcio Safety supervisor has failed to keep pace, we will ask for a replacement prior to the increase in field personnel.  The site housekeeping is relatively good.  We continue in the rainy season.  We will buy and place a mosquito deterrent on the standing water, apparently have a case of Dengue fever on site.  Appears to be airborne allergens causing respiratory distress, one engineer is returning to states for treatment.

Need to develop a means of tracking material from requisition (both local and US), purchase, shipment, and finally to site, that allows Site to know where the material is in the delivery cycle.

The 7EA installation continues, started installation of inlet structure.  The embeds for the 7EA (unit 100) PEECC are available and plan to start installation next week after drilling the embed holes.   Waited for tools, purchasing on hold.

Prepared a CO to Derwick for the crane backfill for setting the 7FA turbine and generator.  This needs  to get approved and start backfill to meet the schedule (schedule slipped 6 days due to lack of concrete from Sidor).  We also need to get approval for repairs to the roads in the lay down yard to allow the trucks to move the generator and turbine to site.

Contractor quality is good, but contractor lack of craft and equipment is causing slippage of the schedule.  We advised the contractor to start staffing up, met with Concorcio to discuss this Thursday, but no response as of today..

Civil contractor started duct bank and manholes, they were delayed for lack of suitable excavation equipment.  Safety had to delay their excavation for manholes due to the overextending of their equipment adjacent to open excavation.

The 7FA anchor bolts are installed by Monday, have waited for concrete since.  QA/QC will conclude the inspections of the 7FA slab by Tuesday.  Will turn on the excavation of the demin and raw water tank fdns, and hope for acceptance of the change order to start moving the treated diesel fuel tank.

1.1 Safety & Regulatory Compliance –

- General Safety will be maintained at all times on site, Concorcio is slow to respond and we will request a new site safety supervisor.  Overhead work started, and night work around open excavations.

- Daily safety audits are now in place, weekly recap to office.

- Contractor will be directed to install permanent Bulletin board will be installed.

- The safety people and contractor are preparing a recap of all man-hours worked.  This will also be useful in determining actual cost vs invoice amounts, since it involves Concorcio Magavatio’s input.

  - Personnel/Staffing –

Cole Franklin (Site Manager)

Keith McMurray (scheduler shared A&B)

Paola Gomez (administrative assist. Local hire)

Patricia Munoz (administrative assist. Local hire)

Daniel Febres (logistics support local hire)

Ysren Gomez (safety supervisor Local hire)

Kyle Rosken (Civil Superintendant)

Mark Hawks (Electrical supervisor)

Felix Martinez (QA/QC supervisor)

Paulo Olivio (Material coordinador)

Jose Martinez (material management local hire)

Jason Byrd (TA)

Jose Garcia Electrical field engineer

1.3 Weekly Accomplishments

- The Oily water separator backfilled

- The 7EA installation continues.

- The 7FA slab is awaiting concrete

- The 7FA silencer is awaiting concrete

- The 7FA stack is awaiting concrete

  - Scheduling Conflicts –

- The duct bank and manholes / hand holes are critical around 7EA.  We will start excavation and have modified the plan to attempt to accelerate the completion.

- Materials for piping and a large portion of the duct bank conduit are now (on ship currently unlading) available at site.

- GSU will start next week, if quote is received from Concorcio for duct bank section below foundation..

- U/G piping contractor is double jointing pipe

1.5– Site Managers Commentary and Amplifying Remarks

We have mobilized the duct bank contractor; they have bent and installed rebar for 2 manholes, poured bases and are forming walls.  The contractor has excavated for third manhole.

The rainy season is a problem, but progress is good.  We need additional Concorcio people and machinery.

Got a new electrical field engineer, he will follow the duct bank contractor in tandem with Mark and Kyle and finally will start take offs for electrical equipment and track drawings.

- Engineering and Design

2.1.1 Received the following drawings this week;

2.1.2 Grounding

- The grounding shown on grounding drawings is not in accordance with the discussion with Sidor regarding grounding of equipment.  This will become a major issue.  Need to put it to bed!

2.1.3 Geo tech membrane treated fuel oil tank

- The geo tech fabric is ordered for fuel oil tank.  Fuel tank rework pending CO to move tank

  - – Site /Civil /Structural

    - The 7FA first pour ready to pour

    - 7FA Stack ready to pour

    - 7FA Silencer pedestal ready to pour

    - Oily water sep back fill complete

    - Excavate waste tanks started.

  - – Mechanical –

    - The 7EA stack erection ongoing

    - The 7EA structure for inlet ongong

2.4 – Electrical –

2.4.1 Duct bank contractor on site 3 manholes started

2.5 – Instrumentation - To Be Completed

2.5.1 EDGI tells us the missing information is due from PES

2.6 – O&M Manuals –

2.6.1 Need to transmit officially one copy 7FA manual.

3. Procurement

3.1 – Purchase Order Requests

- Conduit PO received

- Asked for new quote storage container for material storages,

- Construction power CO for transformer installation delivered, CO issued to Derwick.

3.2 – Equipment & Material Quotations –

3.3 - Purchase Order

  - Several PO Issued this week

4. Contract

4.1 – EPC Contract –

- CO 001 sent of Poor Soils Site B

- CO002 sent for Backfill under crane due to CO001

- CO 003 construction power distribution to site materials

- CO 004 core drilling to Derwick for Sidor provided concrete

- CO 005 issued for core drilling

- CO 006 issued for moving diesel tank

- CO 008 prepared for back fill under crane at 7FA

- CO010 for repairs to lay down road

4.2 – Construction Subcontracts –

4.3 – Proposal & Quotes

5. Construction

5.1 – Schedule

  - Schedule two week look ahead will be issued to Sidor next week.  6 day delay for concrete 7FA

5.2 – Equipment Delivery – in progress

5.2.1 Material issues, early delivery of packing list before receipt of material, and P.O.s are a major problem

5.3 – Mechanical –

5.3.1 7EA build continues

5.4 – Electrical –

5.4.1 duct bank and manholes started

5.5 QA/QC –

- Ongoing inspections concrete, formworks and anchor bolts.

- Started collecting documents for inclusion in T/O manuals

6 Startup & Commissioning –

7 Startup Mobilization - None

Picture 1: 7EA LO console

Picture 2: RW Pipe double-joint

Picture 3: Manhole excavations layout and started

Picture 4: 7EA f house