Table of Contents

1. Executive Summary

EPC

Weekly Report 4 to 10 Sep 2010Date: 12-Sep-10Project: Sidor Site B, Puerto Ordaz Venezuela Written By: Cole Franklin ProEnergy EPC Project Mgr

ProEnergy Site Manager

William Lugo

Cole Franklin

1.1 Safety and Regulatory Compliance

1.2 Personnel/Staffing

1.3 Weekly Accomplishments

1.4 Scheduling Conflicts

1.5 Site Manager Commentary and Amplifying Remarks

2. Engineering and Design

2.1 General Arrangement

2.2 Site/Civil/ Structural

2.3 Mechanical

2.4 Electrical

2.5 Instruments & Control

2.6 O&M Manuals

3. Procurement

3.1 Purchase Order Requests

3.2 Equipment & Material Quotations

3.3 Purchase Order

4. Contracts

4.1 EPC Contract

4.2 Construction Subcontracts

4.3 Proposal and Quotes

5. Construction

5.1 Schedule

5.2 Equipment Delivery Status (expediting report)

5.3 Civil

5.3.1 Site Preparation

5.3.2 Centerline Foundation

5.3.3 GSU Foundation

5.3.4 Auxiliary Foundations

5.4.1 Centerline Equipment Installation

5.4.2 Centerline Piping Installation

5.4.3 Auxiliary Piping Installation

5.4.4 Underground Piping Installation

5.4.5 Above Ground Piping Installation

5.4.6 Balance of Plant (BOP) Piping Installation

5.5 Electrical

5.5.1 Duct Bank Installation

5.5.2 Centerline Electrical Installation

5.5.3 Auxiliary Electrical Installation

5.5.4 Balance of Plant (BOP) Installation

5.6 QA/QC

5.6.1 Equipment Testing

5.6.2 Nonconformity Report

5.6.3 Drawing Revisions

5.6.4 CWI Reports

5.6.5 As-built Drawings

6 Start-Up & Commissioning

6.1 Schedule

6.2 Equipment Status

6.3 Punch list

6.4 Equipment Checkout

6.5 Equipment Functional Test

6.6 Equipment Turnover

6.7 Performance Testing

6.8 Emission Testing

7 Mobilization

7.1 Schedule

7.2 Operating Procedure Development

7.3 Operation Staff Training

7.4 Spare Parts/Inventory Status

1. Executive Summary.

This review is for the week from 4to 10 September 2010.  The safety is relatively good, minor issues with contractors and PPE.

Need to develop a means of tracking material from requisition (both local and US), purchase, shipment, and finally to site, that allows Site to know where the material is in the delivery cycle.  Will review Protrack next week with Bill.

The 7EA installation continues, final stack welding ongoing final stack sections installed.  Need bolts to complete various items and QA close out these non critical issues.  Ready to install 7FA turbine, but have been delayed for crane assembly total of 6 days to date.  Poured the 7FA diffuser section with 2 day delay for lack of sand to prepare the concrete.

Contractor quality is relatively good, contractor commercial issues and lack of contract are causing planning nightmares.  We advised the contractor to start staffing up, met with Concorcio to discuss this.  We are now preparing PO for specific work and delivering to Concorcio, see a potential for incurred cost not defined by PO (ie overhead cost for offices, back fill of existing works not covered by new PO, site trash and water truck, safety personnel, ect)..

Duct bank Civil contractor has poured manholes  and sections of duct bank, expect to utilize these large excavations by installing pipe.  Will meet the contractor next week to discuss cost and finalize payments.

The turbine installation, has slipped.  Sidor installed crane is not complete.  Haul Road for moving the turbine / generator is not completed for 8 Sep.

1.1 Safety & Regulatory Compliance –

- General Safety will be maintained at all times on site, Concorcio is slow to respond and we will request a new site safety supervisor.  Overhead work started, and night work around open excavations for 7FA repairs.

- Daily safety audits are now in place, weekly recap to office.

- Contractor will be directed to install permanent Bulletin board will be installed.

- The safety people and contractor prepared a recap of all man-hours worked, this figure will be incorporated into the sign.

  - Personnel/Staffing –

Cole Franklin (Site Manager)

Keith McMurray (scheduler shared A&B)

Skeila Garcia (doc control and translator)

Paola Gomez (administrative assist. Local hire)

Patricia Munoz (logistics assist. Local hire)

Daniel Febres (logistics support local hire)

Ysren Gomez (safety supervisor Local hire)

Kyle Rosken (Civil Superintendant)

Mark Hawks (Electrical supervisor)

Felix Martinez (QA/QC supervisor)

Paulo Olivio (Material coordinador)

Jose Martinez (material management local hire)

Jason Byrd (TA 7EA 7FA)

Julio Daniels tool room attendant

Jose Garcia Electrical field engineer

Howard Velasquez Civil field engineer

Santiago GE on site this week

1.3 Weekly Accomplishments

- Continued to place and pour duct bank to start GSU 100

- The 7EA installation continues.

- The 7FA fixators ready for 7FA turbine installation

- The 7FA diffuser fdn completed

  - Scheduling Conflicts –

- The duct bank and manholes / hand holes are critical around 7EA.  The field engineers prepared an overlay drawing incorporating all foundations (presently defined) with duct bank and U/G conduit and U/G piping, they have identified solutions for the bust identified, started incorporating the storm drains and drains to the oily water separator as well as fire mains.   U/G piping is started need the piping supervisor at site ASAP

- GSU delayed for duct bank, Coinserma installed duct bank below and adjacent to the GSU  foundation, but have not completed risers to 7EA foundations.

- U/G piping contractor is double jointing pipe, has been released this week to complete welding of 7EA stack so it can be set before Sidor de-mobilizes the crane.  Weld out of stack continues.

- Plan to move Liquid fuels for 7EA into the area this will stop U/G around North side of 7EA.

- Must move on the office and maintenance bldg.  Will layout when the surveyors are back on site, requires moving the spoils from over excavation.

1.5– Site Managers Commentary and Amplifying Remarks

The duct bank contractor has not accelerated, but did finish the pour of second section of duct bank.  The changes and lack of PO is causing some rework.  The contractor has not started work that should be finished and has backfilled requiring re-excavation.

The rainy season hopefully is finished.  We need additional Concorcio people and machinery.  Demobilized the Concorcio site manager, Eduardo will move to B from Site A.  Concorcio advised they will be fully mobilized next week.

Mark and Jose (field engineer) have prepared a take off of electrical drawings and inventoried the materials in laydown yard.  We will send the results to Sedalia next week to order the Delta for the wiring.  Plan to start electrical wiring next week.

Engineering and Design

2.1.1 Received the following drawings this week;

2.1.2 Grounding

- The grounding shown on grounding drawings is not in accordance with the discussion with Sidor regarding grounding of equipment.  This will become a major issue.  Need to put it to bed!

2.1.3 Geo tech membrane treated fuel oil tank

- The geo tech fabric is ordered for fuel oil tank.  Fuel tank on hold pending CO to move tank or remove it from scope.  Plan to have a meeting to resolve this next week.  We have put into Contractor Client meeting minutes we are proceeding as if this issue is resolved.

  - – Site /Civil /Structural

    - The 7FA diffuser poured.

    - Prepared for 7FA turbine install, grouted fixators.

    - Poured several parts of duct bank.

  - – Mechanical –

    - The 7EA stack weld out near complete

    - 7EA piping ongoing

2.4 – Electrical –

2.4.1    Duct bank contractor on site, ongoing.

2.4.2    Take off completed for all identified Hi Voltage and Medium Voltage cable

2.4.3    Completed review of transformers against drawings, required we open the crates.

2.4.4    Verified the motor and finished meggering all on site.

2.5 – Instrumentation - To Be Completed

2.5.1 EDGI tells us the missing information is due from PES

2.5.2 Prepared a list of all electrical electronic parts removed and sent to Termozuila

2.6 – O&M Manuals –

2.6.1 Need to transmit officially one copy 7FA manual.

3. Procurement

3.1 – Purchase Order Requests

- New quote storage container for material storages, released, anticipo paid

- Construction power transformer installation started, awaiting outage to connect.

- Anchor bolts for hi voltage yard and buildings

3.2 – Equipment & Material Quotations –

1.

3.3 - Purchase Order

Demin and Raw tank PO issued to same contractor as A

4. Contract

4.1 – EPC Contract –

- CO 001 sent of Poor Soils Site B

- CO002 sent for Backfill under crane due to CO001

- CO 003 construction power distribution to site materials

- CO 004 core drilling to Derwick for Sidor provided concrete

- CO 005 issued for core drilling

- CO 006 issued for moving diesel tank

- CO 008 prepared for back fill under crane at 7FA

- CO010 for repairs to lay down road

- CO for Paint

4.2 – Construction Subcontracts –

1. Change Order to Coinserma

2. Contract negotiations with Concorcio on hold, will attempt to get them back to table.

4.3 – Proposal & Quotes

1. Received quote from Ceimusa for Office and maintenance building.

5. Construction

5.1 – Schedule

  - Schedule two week look ahead will be issued to Sidor next week.

  - 2 day delay for concrete 7FA

  - 6 day delay for the setting of Turbine for 7FA

5.2 – Equipment Delivery – in progress

5.2.1 Material issues, early delivery of packing list before receipt of material, and P.O.s are a major problem

5.3 – Mechanical –

5.3.1 7EA build continues

5.4 – Electrical –

5.4.1 duct bank and manholes ongoing

5.5 QA/QC –

- Ongoing inspections concrete, formworks and anchor bolts.

- Started collecting documents for inclusion in T/O manuals

- Weld map prepared 2 production x-rays taken, need film reader to review the x-ray film.

6 Startup & Commissioning –

7 Startup Mobilization - None

Picture 1: 7FA Turbine move

Picture 2: 7FA Crane ready

Picture 3: 7FA Diffuser ready for concrete final QC checks

Picture 4: transformers checked against drawings