Table of Contents

1. Executive Summary

EPC

Weekly Report  15 -21 May 2010Date: 21-May-10Project: Sidor Site B, Puerto Ordaz Venezuela Written By: Ted York ProEnergy EPC Project Mgr

ProEnergy Site Manager

ProEnergy Construction MgrWilliam Lugo

Cole Franklin

Ted York

1.1 Safety and Regulatory Compliance

1.2 Personnel/Staffing

1.3 Weekly Accomplishments

1.4 Scheduling Conflicts

1.5 Site Manager Commentary and Amplifying Remarks

2. Engineering and Design

2.1 General Arrangement

2.2 Site/Civil/ Structural

2.3 Mechanical

2.4 Electrical

2.5 Instruments & Control

2.6 O&M Manuals

3. Procurement

3.1 Purchase Order Requests

3.2 Equipment & Material Quotations

3.3 Purchase Order

4. Contracts

4.1 EPC Contract

4.2 Construction Subcontracts

4.3 Proposal and Quotes

5. Construction

5.1 Schedule

5.2 Equipment Delivery Status (expediting report)

5.3 Civil

5.3.1 Site Preparation

5.3.2 Centerline Foundation

5.3.3 GSU Foundation

5.3.4 Auxiliary Foundations

5.4.1 Centerline Equipment Installation

5.4.2 Centerline Piping Installation

5.4.3 Auxiliary Piping Installation

5.4.4 Underground Piping Installation

5.4.5 Above Ground Piping Installation

5.4.6 Balance of Plant (BOP) Piping Installation

5.5 Electrical

5.5.1 Duct Bank Installation

5.5.2 Centerline Electrical Installation

5.5.3 Auxiliary Electrical Installation

5.5.4 Balance of Plant (BOP) Installation

5.6 QA/QC

5.6.1 Equipment Testing

5.6.2 Nonconformity Report

5.6.3 Drawing Revisions

5.6.4 CWI Reports

5.6.5 As-built Drawings

6 Start Up & Commissioning

6.1 Schedule

6.2 Equipment Status

6.3 Punch list

6.4 Equipment Checkout

6.5 Equipment Functional Test

6.6 Equipment Turnover

6.7 Performance Testing

6.8 Emission Testing

7 Mobilization

7.1 Schedule

7.2 Operating Procedure Development

7.3 Operation Staff Training

7.4 Spare Parts/Inventory Status

1. Executive Summary.

This review is for the week from 15 May to 21 May 2010.  Safety is good, housekeeping is relatively good.  Due to commercial issues the contractor will not send additional manpower or materials to site to support. They also stated they would not start a second shift at this time.  The client stated in a side conversation in the Tuesday contractor meeting that they are considering hiring an engineering firm to complete the designs instead of proceeding with EDG due to the poor quality and lack of urgency that has been shown in their opinion. The PES Site offices are complete and PES has taken possession.

The lack of engineering drawings continues to be a problem. Engineering drawings show a lack of review and attention to details. Material deliveries are still not fully explained and the Bill of Materials for Piping, Electrical, Instruments, and equipment are not available at site. Engineering did provide a copy of the piping specification this week.

The new unisorb embeds for 7EA (2- 115 & 1- 116), to replace the ones found damaged in Site A, still have not arrived to the site.  We have proceeded with the original plates and pour the foundation this following week.

Contractor quality is good, but contractor documentation for quality is a weakness.  The contractor’s workforce is showing a good mix of quality craftsmen and upper level supervision.  The contractor’s foreman level is a little weak.  Contractor has suspended work on everything except the 7EA in order to use the limited resources and materials he has on site. This is unfortunate since we now have additional designs and materials are beginning to arrive to the site. We started performing material take offs and preparing field purchase orders to support the project execution.

  - Safety & Regulatory Compliance –

- General Safety will be maintained at all times on site.

- Daily safety audits are now in place, weekly recap to office.

- Contractor installed safety signs on site, marked out traffic lanes to eliminate outside traffic from site and installed a safety bulletin board in their lunch room.

  - Personnel/Staffing –

Cole Franklin (Site Manager)

Ted York (Construction manager)

Melinda Siros (document control)

Keith McMurray (scheduler)

Paola Gomez (administrative assist. Local hire)

Patricia Munoz (administrative assist. Local hire)

Daniel Febres (logistics support local hire)

Ysren Gomez (Local hire safety supervisor)

Kyle Rosken (Civil Superintendant returned to B Wednesday)

Hal Schulmeyer (Civil Supervisor site B)

Mark Hawks (Electrical supervisor returned to B Wednesday)

Felix Martinez (QA/QC supervisor currently shared A & B)

Ed Dubois (QA/QC tech currently shared A & B)

Dennis Maloney (Turnover engineer currently acting as Safety Supervisor B)

Paulo Olivio (Material coordinator B) left site for family emergency

Herman Flores (material control Local hire presently Site A)

Jose Angel gonzales (material control Local hire)

Francisco Gomez (tool room control Local hire presently Site A)

1.3 Weekly Accomplishments

- The 7EA foundation works continue, contractor completed installing anchor bolts, continued installing embed plates, and continued installing the top rebar mat.

- The contractor installed their site trailer and connected it to the power supply.

- Contractor poured the foundation for the construction power supply transformer and ran the power cable to their tool room.

- Completed the structural fill for the Treated Fuel Tank. Work was suspended on 5-19-10 due to commercial issue and the freezing of additional manpower and material. Client requested the work to be suspended till the separation issues from inhabited facilities, ignition sources, future tank, etc required by Venezuelan and API-650 codes is resolved in contractor meeting on 5-20-10.

- Contractor began installing concrete forms for the 7FA. Work was suspended on 5-19-10 due to commercial issue and the freezing of additional manpower and material.

- Completed back fill of Oily Water separator. Work was suspended on 5-19-10 due to commercial issue and the freezing of additional manpower and material.

1.4 – Scheduling Conflicts –

- Received revised manhole details, handhold details and duct bank plot plan. Comments have been returned to engineering and being reviewed.

- Received underground piping drawings, review and provided comments to engineering. Design is current around 1.5 to 1.9 meters and below the bottom of adjacent foundations. Excavations in these locations must be performed prior to installation of the foundations.

- The foundations adjacent to the duct banks cannot be installed that have excavations to a lower elevation compromising the installed foundations.

- Balance of 7FA drawings were received on 5-20-10.

- The foundation drawings IFC continue to be issued.  The present quality of the drawings was been recapped in a spreadsheet.  This spread sheet has been published. PES reviewed the 7FA equipment list and informed engineering that it appears that all of the equipment is not represented on the plot plan. PES is concerned that underground utilities are not complete in the current designs. Engineering is reviewing.

- The general arrangement will change.  The hold on the drawings was due to expansion of the Treated Fuel Tank retention area which now impedes into the site trailer location.  This effectively stops all but the treated fuel tank, the oily water separator, the 7EA, and 7FA.  The location plan for the duct bank indicates the foundations available are on top of or very near the duct bank.

- The Bill of Materials and equipment list for all materials and the P.O. log for all materials ordered are now a necessity to ensure we do not lose more time for material delivery delays. Materials deliveries continue to be an issue for the site. Due to the lack of information on the packing lists and packaging we are having a hard to determine what we are receiving and where it goes. This is highly impacting the amount time required.

1.5 – Site Managers Commentary and Amplifying Remarks

- The duct bank and underground are still an issue.  Due to the sandy composition of the soils, the excavation for duct bank and underground utilities and storm drains, will need special attention.  If we excavate near the foundation for underground, and it is below the foundations bottoms, we will have subsidence of the soils.  We need to place the U/G now.  Doing a material take off at site for U/G piping and conduit for duct bank to locally purchase.  We are short on duct bank materials, conduit and intermediate support for the conduit.

- I recommend the contractor be allowed to remain at present levels of staffing.  Our efforts to increase their manpower loading have meet with little or no success.  This is driven by lack of engineering and the lack of bulk material delivery dates.  If the engineering does not arrive in a manner that will support the site we will be demobilizing a part of their staff for lack of work within the next two weeks.

- Work has been suspended by the contractor on 5-19-10 due to commercial issue and the freezing of any additional manpower, materials and he will not consider starting a second shift at this time till these issues are resolved.

2 Engineering and Design

2.1 – Received the following drawings this week;

  - Balance of 7FA Foundation Drawings.

  - Revised Plot Plan Manholes and hand hole sketch. Provided comments to engineering.	Storm Drain Profile and Detail Drawings

  - Control Schematics

  - One Lines

  - Electrical Grounding Plot Plan

  - Water Treatment Plant Floor Drains

  - Revised Underground Piping Drawings. Reviewed and comments to engineering.

  - 7EA GSU Plan and Conduit Penetrations, Engineering to revise adding conduit elevations and GTG-100 in title block.

  - Plant B Foundation Location Plan; added coordinates for foundations, still missing foundation some locations, cut top of site plot plan off (doesn’t effect foundations) and  TOC schedule added is missing some of the associated unit numbers.

  - Waste Tanks Foundation Plan and Sections; Revised orientation.

2.1.1 – Started installing lower rebar mat and concrete forms. Suspended work on the 7FA foundation due to commercial issues on 5-19-10.

2.1.2 – Site /Civil /Structural – The 7EA anchor / embeds installation continues.  7th May we noted the conduit drawings were not correct.  Spoke with engineering regarding this and they verified from the daily report photos we are installing correctly, but not according to the drawings.  Drawings are to be revised.

2.1.3 - The grounding shown on grounding drawings is not in accordance with the discussion with Sidor regarding grounding of equipment.  This will become a major issue.  Site will red line drawings to open discussion of final resolution.

2.1.4 The water stop for the oily water and waste tanks was resolved.

2.3 – Mechanical –

2.3.1 The 7EA turbine replacement thrust pin plate is being fabricated. Forecast delivery is 5-29-10.

2.4 – Electrical –

2.4.1 Duct bank drawings were issued and engineering is working on comments from the site.

2.5 – Instrumentation - To Be Completed

2.6 – O&M Manuals –

2.6.1 7 EA O & M from another site on site.

3. Procurement

3.1 – Purchase Order Requests

- After discussion at site, due to the receipt of materials not clearly identified by site and by equipment, we will now include the following in all material requisitions:

- The Site “A or B”

- Associated equipment numbers or Balance of Plant equipment or system

- Material specification if applicable

- Who generated the requisition

- Contact information for delivery

- A copy of the P.O. for review after it is produced and before it is released.

- Material certifications

- The above will allow QA to assure we have the proper material and segregate it if necessary.

3.2 – Equipment & Material Quotations –

- In the process

3.3 - Purchase Order

3.3.1– Copies of all P.O. to originator after issued and tracking of same by logistics.

3.3.2 – Preparing a list of materials for local purchase for U/G piping and duct banks.

4. Contract

4.1 – EPC Contract –

4.2 – Construction Subcontracts –

  - Negotiation ongoing in preparation for actualizing contract, all works currently performed direct supervision

4.3 – Proposal & Quotes

  - Prepared and issued contract RFP for supplying power to the lay down yard and modifying two sea containers into an office and environmentally controlled storage. Two proposals were received and are under review.

5. Construction

5.1 – Schedule

- Schedule is being prepared showing the estimated man load to support the ongoing negotiations with the client. Disclaimers will be noted on the bottom for design status, designs support required and material delivery support required; otherwise schedule will slip.

5.2 – Equipment Delivery – in progress

5.3 – Mechanical –  (Work was suspended on 5-19-10 except for the 7EA due to commercial issues)

  - Completed back fill of Oily Water Separator.

  - Completed back fill of Treated Fuel Tank.

  - Continuing on 7EA foundation.

  - Started installation of concrete forms and lower rebar mat for the 7FA.

5.4 – Electrical –

  - Completed installation of embedded grounding for 7EA foundation.

5.5 QA/QC –

- Ongoing inspections on 7EA foundation.

- Discovered lack of documentation for 7EA anchor bolts or proper markings on bolts and nuts. Investigation is in process.

6 Startup & Commissioning –

  - The blank turn over manuals are being prepared for both sites.

7 Startup Mobilization - None

Picture 1: Installing Embeds and Upper Rebar Mat for 7EA Foundation

Picture 2: Installing Concrete Forms and Lower Rebar Mat for 7FA Foundation

- Picture 3: Completing Back Fill for Treated Fuel Tank.

Picture 4: Completed Back Fill of Oily Water Separator.

Picture 5: Installing Construction Power Line to Site Tool Trailer and Transformer Foundation.

Picture 6: Installing Embedded Grounds in 7EA Foundation.