CVG SIDOR POWER PROJECT SITE “B”

DATE: 18 May 2010, Tuesday PROJECT #: 410-3203 SITE MANAGER: Cole Franklin

TEMPERATURE:  77 F

RANGE: 74 to 85

SITE CONDITIONS: Cloudy

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Project Mgr (A&B)(R&R)

Bob Hooper – Project Mgr (A&B)

Cole Franklin - Site Manager

Ted York - Const Manager

Melinda Siros - Doc Control (R&R)

Dennis Maloney – Safety Mgr TO/Coord

Ysrin Gomez – Local Safety

Jason Bird - TA/7EA (A&B)

Hal Schulmeyer - Civil Supv

Edward Dubois – QA/QC (A&B)

Keith McMurray - Scheduler

Felix Martinez - QA/QC (A&B)

Mark Hanks - Electrical Supt

Kyle Roskan - Civil Supt

MATERIAL SUPPORT

Jose Angel Gonzales – Materials

David Jackson – Material (7FA Invent)

Paul Oliva – Materials

ADMIN SUPPORT:

Daniel Febres – Logistics

Paulo Gomez - Admin

Patricia Munos - Admin

Skeila Garcia - Translator

SUBCONTRACTOR PERSONNEL:

General Superintendant        1

Foremen			   2

Electricians                            0

Operators                              5                         Surveyor                                1

Carpenters                           14                          Surveyor Helper                    2

Oiler Helper                           1

Crane Operator                     0                           Laborers                                6

Truck Drivers                         2

Concrete Finishers		   0

Oilers                                     1

Plumbers                               0                        Iron Workers			  14

Helpers                                  2

Welders                                 2			Total:				  53

- GENERAL ITEMS:

  - We are getting close to a work stoppage due to the lack of IFC design drawings. We are in continuous discussions with EDG on this issue.

  - Safety issues are also covered with the contractor in the bi-weekly meeting.

  - Received proposal for modifying sea containers for lay down area office, temperature controlled storage and running power to area. Offer is under review. Provided RFP to second contractor, Consorcio Juvenca, for estimated proposal.

  - Port reopened to incoming ships, 5-17-10.

- CLIENT ISSUES/CONCERN:

  - Progress on Foundation 7EA and 7FA.

  - Underground piping and duct bank drawings scheduled for review 31 Mar 10.  We received the manhole details, 5-12-10. The elevations of the duct banks are not given. Materials delivery will seriously impact us being able to start this work.

  - Waiting on trash bins from Sidor for site lay down area. We are going to discuss this with Sidor.  Site will check availability of a local provider and prepare a field PO to correct this issue if local provider is available.

  - Sidor to produce fire water flow rates for Plant B, no forecast date provided.

  - Sidor was very upset today in the bi-weekly contractor meeting due to the lack of progress on Plant B. They cited design as a major problem and were overheard talking about bringing in an engineering firm to take over for EDG.

- CIVIL:

  - Trailer supplier did not work on the trailers today. He was notified that we will hold the invoice for payment for everyday we are delayed in taking occupation of the trailers due to the work not being completed. Supplier is scheduled to return tomorrow.

- CONCRETE FOUNDATIONS:

  - Continued installation of top rebar mat and continued on generator form modifications for 7EA foundation.

  - Continued installation of anchor bolts for 7EA foundation.

  - Completed installation of Unisorb embeds for 7EA.

  - Replacement 7EA Unisorb base plates are being held by customs due to a discrepancy in shipping documents, 5-7-10. PES has given contractor directions to proceed with the existing Unisorb plates, 5-15-10. Forecast arrival to site 5-17-10 at 1530 hours. Port was reopened today and the Dolphin is docked.

  - Performed walk down with heavy haul provider at 0915 hours 5-18-10 on site for 7EA and 7FA. Staging area was determined for the crane reviewing setup location for crane.

  - Continued with lower mat rebar and concrete forms for 7FA.

  - Continued with structural fill for Treated Fuel Tank.

  - Completed excavation and structural fill on Oily Water Separator.

- MECHANICAL:

  - 7EA generator replacement jib base plate is being fabricated in Sedalia. Tom Koontz will ship by air freight to site as soon as it is complete. Current forecast is 5-22-10.

  - Preparing to give 7EA stack repairs and the underground piping to ISI contracting company due to no response from Concorcio Megavatio. Waiting on submittal of their QA Plan and Welding procedures from ISI.

- PIPING:

- ELECTRICAL:

  - Pull box details have been approved and issued. Contractor was instructed to begin to proceed with pre-casting units and to begin a second shift. Material deliveries is seriously impacting us being able to start duck bank installations.

  - Due to the lack of material PES is prepared and issued a local purchase request for electrical materials required to perform grounding in 7EA. PES is preparing a local purchase request for electrical materials required for the start of the duct banks. Current inventory on Ship Dolphin which docked at Puerto Ordaz today is short for the duck banks at the 7EA area.

  - Grounding design and materials is impacting 7EA foundation completion. PES is going to proceed with fewer embedded grounds and above concrete ground routing as performed on previous projects.

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS: - GE TA for 7FA inventory resumed.

- CRITICAL AREAS OF CONCERN:

  - Changes in designs are impacting project progress/completion.

  - Shortage of cement is affecting the scheduling of foundations. Sidor has requested a 4-5 day prior notification for concrete so they will have time for the cement to be loaded into the hoppers and cool down to support the pours.

  - SAFETY:

    - Concorcio Megavatio installed a bulletin board in lunch rooms showing. Job site information board has been assembled.

    - Concorcio Megavatio began installing warning labels on equipment and machinery, 5-18-10.

    - Weekly safety meetings with Sidor, Concorcio and Pro Energy are scheduled for every Tuesday at 1000 hours at the Plant “A” contractor’s office.

    - Site safety meetings are scheduled for every Monday at 0700 hours at the Plant “A” contractor’s office.

  - OUTSTANDING DRAWINGS:

    - Plot plans and foundation drawings all need to be on the same foot print.

    - 20-01 sheet 1 rev 11 Plant B Foundation Location Plan; added coordinates for foundations, still missing foundations, some foundations missing locations, cut top of site plot plan off (doesn’t affect foundations) and  TOC schedule added is missing some of the associated unit numbers, 5-15-10.

    - Duct Bank. Forecast 5-11-2010 Received pull box and manhole TOC sketch with no coordinates, 5-13-10. Due to the impacts to schedule to date PES is planning on proceeding with sketch only.EDG stated in engineering meeting this morning that the duct banks are all moving, forecast 5-19-10.

    - Underground piping. Forecast 5-5-2010. Received revised 5-14-10; Drawing are under review. Missing 101, 104, 105, 106, 111, 115, 116, 120, 121, and 122, 5-15-10.

    - .

    - Storm Drain. Forecast 5-12-10. Received 5-13-10 on grading plan. Details are required for location, elevation, catch boxes, etc.

    - 7EA GSU foundation section views. Step Up Transformer Plan and Conduit Penetration Details 20-04 sheet 4; Title on sheet 4 does specify GTG-100 and sheet 3 not issued, 5-15-10. Step Up Transformer Grounding Plan 20-04 sheet 5; still has excessive ground penetrations in foundations and does specify GTG-100, 5-15-10.

    - .

    - 7FA GSU foundation detailed drawings, forecast 5-21-10.

    - 7FA centerline drawings, Accessory Module, Liquid Fuel Module and anchor bolt schedule missing. Forecast 5-18-10

    - Balance of foundation details. 5-25 -2010. Received WTP, Office, Foam/Pump and Gas Compressors, 5-13-10, which are under review.

    - EDG determined the only problem area for the dog bone water seal is in the Oily Water Tank Foundation. Issue was resolved.

    - Grounding Plan (Drawings are under review and PES has some issues and concerns with the designs).

    - 20-60 sheet 13 rev 0; Issued with “Hold Compressor Has Changed”. Revision number was not changed on drawing so there are now two revision 0’s.

    - EDG forecast all designs to be complete by 5-31-10.

Note: Email sent by Cole Franklin to Mike Holland on 4-30-10 regarding priorities and needs. Luis Acevedo forwarded email from Mike Holland with forecast dates and items requiring equipment information. Pro Energy is reviewing the EDG drawing log with what has been issued to the site. Results have been issued.

  - ISSUED DRAWINGS:

    - Control Schematics.

    - One Lines

    - Electrical Grounding Plot Plan.

- PICTURES:

Picture 1: Installing Top Mat of Rebar for 7EA Foundation.

Picture 2: Installing Concrete Forms for 7FA Foundation.

Picture 3: Completed Installation of Structural Back Fill for Oily Water Separator.

Picture 4: Installing and Compaction Testing Structural Fill for Treated Fuel Tank.