# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 26 May 2010, Wednesday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  79 F

RANGE: 74 to 86

SITE CONDITIONS: Partly Cloudy and a Light Breeze

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Project Mgr (A&B)

Cole Franklin - Site Manager

Ted York - Const Manager

Melinda Siros - Doc Control

Ysrin Gomez – Local Safety (Local)

Jason Bird - TA/7EA (A&B)

Keith McMurray - Scheduler (A&B)

Felix Martinez - QA/QC (A&B)

Mark Hanks - Electrical Supt

Kyle Roskam - Civil Supt

MATERIAL SUPPORT:

Jose Angel Gonzales – Materials (Local)

Paul Oliva – Materials

ADMIN SUPPORT:

Daniel Febres – Logistics (Local)

Paulo Gomez – Admin (Local)

Patricia Munos – Admin (Local)

Skeila Garcia – Translator & Doc Control (Local)

SUBCONTRACTOR PERSONNEL:

General Superintendant        1

Foremen			   2

Electricians                            0

Operators                              0                        Surveyor                                1

Carpenters                           14                          Surveyor Helper                    2

Oiler Helper                           0

Crane Operator                     0                           Laborers                                3

Truck Drivers                         0

Concrete Finishers		   0

Oilers                                     0

Plumbers                               0                        Iron Workers			  14

Helpers                                  2

Welders                                 2			Total:				  41

- GENERAL ITEMS:

  - We are getting close to a work stoppage due to the lack of IFC design drawings. We are in continuous discussions with EDG on this issue.

  - Received proposal for modifying sea containers for lay down area office, temperature controlled storage and running power to area. Offer is under review. Provided RFP to second contractor, Consorcio Juvenca, for estimated proposal.

  - All new purchase orders and contracts have been put on hold till the commercial issues are resolved. Superintendents are going to breakup drawings using a grid the plot plan and generate purchase orders accordingly during the work slow down.

  - Held Concorcio Mega vatio meeting, 5-25-10. Concrete for Saturday 7EA pedestal pour was confirmed with Sidor representative. Order was issued to Sidor immediately after the meeting. Sidor informed us 5-24-2010 that Saturday pour may be in jeopardy if concrete plant doesn’t receive an order for minimum 100m. This appears to be a contract issue between Sidor and the concrete plant. This would be a schedule impact to the project.

- CLIENT ISSUES/CONCERN:

  - Progress on Foundation 7EA and 7FA.

  - Underground piping and duct bank drawings scheduled for review 31 Mar 10.  Materials deliveries are seriously impacting the ability to start this work.

  - Waiting on trash bins from Sidor for site lay down area. We are going to discuss this with Sidor.  Site will check availability of a local provider and prepare a field PO to correct this issue if local provider is available.

  - Sidor to produce fire water flow rates for Plant B, no forecast date provided.

  - Sidor was very upset in the bi-weekly contractor meeting 5-18-10 due to the lack of progress on Plant B. They cited design as a major problem and were overheard talking about bringing in an engineering firm to take over for EDG.

- CIVIL:

  - Refrigerator was received. The shelves for document control are forecast for delivery on 5-28-10 for the Site B Office.

  - When locking up at night leave the A/Cs on for the electronic equipment. Lights will be left on due to the problems with turning them on in the mornings. The lights were inspected by PES electrical and they use very little electricity so it is not an issue to leave them on 24 hours a day.

- CONCRETE FOUNDATIONS:

  - Completed installation of top rebars mat and form modifications for 7EA foundation.

  - Completed installation of anchor bolts for 7EA foundation.

  - Contractor informed us that the owner of the company has changed his mind and will not supply any additional people or materials.

  - QA/QC inspections are in process on 7EA.

  - Resumed work on 7FA on 5-20-10.

  - Continued installing bottom rebar mat for the 7FA foundation. Started installation of vertical rebar. Contractor informed us that the owner of the company has changed his mind and will not supply any additional people or materials. The work is progressing very slowly due to the lack of manpower and materials.

- MECHANICAL:

  - 7EA generator replacement jib base plate is being fabricated in Sedalia. Tom Koontz will ship by air freight to site as soon as it is complete. Current forecast is 5-29-10.

  - Requested ISI to provide insurance certifications.

- PIPING:

- ELECTRICAL:

  - On 5-22-10 contractor stated he would start survey on manholes 5-24-10.

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS: - Plant B schedule is being modified to reflect current design. Forecast completion is 5-28-10.

- CRITICAL AREAS OF CONCERN:

  - Changes in designs are impacting project progress/completion.

  - Shortage of cement is affecting the scheduling of foundations. Sidor has requested a 4-5 day prior notification for concrete so they will have time for the cement to be loaded into the hoppers and cool down to support the pours.

  - Concorcio Megavatio will not supply additional manpower or materials due to commercial issues.

  - Due to the commercial issues PES has begun releasing the staff of the site.

  - SAFETY:

    - Concorcio Megavatio reported job site information board was assembled and ready to bring to site for installation.

    - Concorcio Megavatio has not started installing warning labels on equipment and machinery. Formal letter will be written to contractor on this issue if not addressed by the next site meeting.

    - Weekly safety meetings with Sidor, Concorcio and Pro Energy are scheduled for every Tuesday at 1000 hours at the Plant “A” contractor’s office.

    - Site safety meetings are scheduled for every Monday at 0700 hours at the Plant “A” contractor’s office.

  - OUTSTANDING DRAWINGS:

    - Plot plans and foundation drawings all need to be on the same foot print.

    - 20-01 sheet 1 rev 11 Plant B Foundation Location Plan; added coordinates for foundations, still missing foundations, some foundations missing locations, cut top of site plot plan off (doesn’t affect foundations) and  TOC schedule added is missing some of the associated unit numbers, 5-15-10. Engineering informed us that there will be some drawing sheet numbers not used. They will clarify this on their drawings to help eliminate confusion.

    - Duct Bank. Forecast 5-11-2010 Received pull box and manhole TOC sketch with no coordinates, 5-13-10. Due to the impacts to schedule to date PES is planning on proceeding with sketch only.EDG stated in our daily meeting 5-19-10 that only the south east portion of the duct banks is moving away from the foundations and that the TOC for the duct banks is being added to the drawings forecast for issue on 5-19-10. After review of the drawings Pro Energy requested EDG to assess depth of conduits leaving hand holes, perform an evaluation for areas where load bearing equipment will be set up (cranes, forklifts, etc) over duct banks and if RGS conduit should be used in these areas with steel reinforced cage, 5-20-10. Coordinances were requested to be added to the drawings, 5-25-10.

    - Underground piping. Forecast 5-5-2010. Received revised 5-14-10; Drawing were reviewed with EDG and comments have been forwarded to their office for resolution. Forecast delivery 5-24-10. Engineering made a guess that the new revision should be released today. They were unsure when they would be issued, 5-25-10.

    - 7EA GSU foundation section views. Step Up Transformer Plan and Conduit Penetration Details 20-04 sheet 4; Title on sheet 4 does specify GTG-100 and sheet 3 not issued, 5-15-10. Step Up Transformer Grounding Plan 20-04 sheet 5; still has excessive ground penetrations in foundations and does specify GTG-100, 5-15-10. GSU delivery is forecast for 6-5-10 and EDG was requested in meeting 5-19-10 to complete the designs so we can be ready to set upon cure of foundation. Conduits appear to be interring the foundation in the wrong location, 5-25-10.

    - 7FA GSU foundation detailed drawings, forecast 5-21-10. GSU delivery is forecast for 6-5-10 and EDG was requested in meeting 5-19-10 to complete the designs so we will be ready to set upon cure of foundation. Revision forecast for 5-25-10. Engineering was unsure if the revision would be issued today, 5-25-10.

    - Balance of foundation details, 5-25-2010. Engineering stated they did not know when the balance of the foundations would be issued, 5-25-10.

    - Grounding Plan (Drawings are under review and PES has some issues and concerns with the designs).

    - 20-60 sheet 13 rev 0; Issued with “Hold Compressor Has Changed”. Revision number was not changed on drawing so there are now two revision 0’s.

    - EDG forecast all designs to be complete by 5-31-10. EDG stated completion date is going to slip and will supply a new date. Engineering stated in today’s meeting, 5-25-10, that they did not know when the designs

would be completed.

  - ISSUED DRAWINGS:

    - 0919-20-001 Sheet 1 rev 12, Foundation Location Plan

    - 0919-60-041 Sheet 21 rev 1, Control Schematics – GTG-100 Fuel Gas Compressor #2

- PICTURES:

Picture 1: Final QAQC Checks for the 7EA Foundation.

Picture 2: Installing Vertical Rebar for the 7FA Foundation.