# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 2 October, 2010, Saturday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  84 F

RANGE: 78 to 94

SITE CONDITIONS: overcast, hot, humid

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

Williams Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Unfilled Mechanical/Piping (local ASAP)

Unfilled mechanical / piping expat ASAP

Mark Hanks - Electrical Supt

Jose Garcia - Elect. Field Eng.

Kyle Roskam - Civil Supt

Howard Velasquez-Civil Field Eng

Felix Martinez-QA/QC

Jason Bird - 7EA TA

Paul Olivo – Material

Unfilled T/O coordinator

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Julio Daniels 	– tool room (Local)

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila García – Translator / Doc Control

SUBCONTRACTOR PERSONNEL: no work

Concorcio Megavatio

General Superintendant		1

Safety					1

Foremen				2

Electricians				2

Operators				1                    Surveyor				1

Carpenters				5

Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				6

Truck Drivers				2

Concrete Finishers			0

Oilers					0

Plumbers				0

Iron Workers				5

Helpers

Welders				1

Total:					29

SUBCONTRACTOR PERSONNEL: ISI

General Superintendant		0

Safety					1

Foremen				1

Operators				1

Oiler Helper				0

Welders                                         6

Millwrights

Crane Operator			1                           Laborers				0

Truck Drivers				1

Mechanic	      			4

Helpers				6

Pipe fitter                                       6

Total                                             32

- GENERAL ITEMS

  - No site power all day, Sidor has problem with damage to high voltage incoming line, not related to tie in of site power.

  - Removing water from excavations by ISI

  - Small crew installing 7EA expansion joint and welding pipe

  - 7FA, crane disassembly not started after setting.  Need to get crane disassembled and backfill removed to continue with installation.

  - Pipe repairs to pre fabbed spools, need QA/QC for work performed in Sedalia, no NDE reports (Tom Koontz).

  - Need to review model contract and get contractors to table to formalize contracts.  We are preparing a line item scope of work for ISI, Concorcio, and Sialca

  - Need status of delivery for de min and raw water tank materials

- CLIENT ISSUES/CONCERN:

  - Access to GSU for service (grating over containment area) Chem. grate manufacturer came to site to view GSU at Site A and prepare a quote and design. Ongoing

  - Building design for office maintenance building, PSC, and MCC attached to compressor building.

  - Need crane moved at 7FA and backfill removed.  Sidor did not approve Change Order to build crane pad and subsequently remove fill, removal is in their scope.

- CIVIL:

  - Spoke with David Miner (Maracaibo), will prepare a quote and can start with approved materials immediately after receipt of PO for compressor bldg anchor bolts.

  - Removing excess spoils from High Yard area to offsite location

- CONCRETE FOUNDATIONS:

  - Backfill ongoing compressor bldg, anchor bolt RFQ prepared.  Stopped for rains

  - Ongoing forms and rebar for Raw Water Tank Foundation stopped for cleanup after rains

  - Extending spare conduits on 7FA placed lean concrete for Accessory Module Foundation stopped for cleanup after rains

  - Laid out excavation boundaries for Unit #100 GSU today, stopped excavation.

- MECHANICAL:

  - Started LO prep for flush, necessary to move disassembled materials from Site A to Site B

  - Paint spec. to Sedalia for review to prepare scope and RFQ.  Received a material spec, but this requires purchase of material in US and then testing to see if it is acceptable. Unresolved

  - Prepare a QA plan for tanks.  Issued scope of work for Tank PO. QA/QC plan received first draft, returned with comments.

  - Need copy of GE drawings for 7FA.

  - Met with potential building contractor to review the schedule he is proposing and outline of the method of contracting.  He is offering a discount for all buildings.  HE is offering to quote EPC, the design of new foundation for office maintenance bldg, modifications to steel received at site for office maintenance bldg, and installation of Office and Maintenance building.

- PIPING:

  - Piping installation is started, but NCR issued for materials.  Received PES QA Plan and find MTR required per plan.

  - Need a film viewer.  Will purchase US not available here, they read film with flashlight.  Have doubts to the veracity of the x-ray readings.

  - ISI continued underground piping this week.  Fabbing spools for tie points.  Preparing ISO’s from drawings produced at site.

- ELECTRICAL:

  - Plan to open all MCC and compare them against drawings next week, Sidor provided space, need to move MCCs to space.

  - Cathodic protection contractor, received quote need to issue contract after review of drawings.  Dwgs not received today.

  - Cable schedule for hi and med voltage cables completed.  Will send list to EDGI for review and comparison against their take off.

  - Review and audit of electrical drawing against equipment nomenclature tags ongoing, all transformers checked will check motors and additional materials as received. Ongoing

  - Prepared a scope of work for electrical contract with local contractor, about 80% complete.

  - Need to prepare a CO for delays in energizing temp const power to site.  De mob of equipment to Site A, shut down const power at site.  Met with Sidor late afternoon to jointly conduct punch list for energizing. Ongoing

  - Daniel Gonzalez showed Mark and Jose the space to open and modify as necessary the MCC panels.

- INSTRUMENTATION AND CONTROLS:

9.    SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works two shifts or a 12 hours shift.  Need authorization to work more hours.

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (60%)

Complete

- Civil Foundations Complete (25%)

Sep 15, 2010 (*) do not have all drawings for foundations.  We expect at least 7 weeks delay, schedule review continues.

- Electrical/Mechanical Complete (10%)

Dec 3, 2010 (*) expect at least 7 weeks due to lack of drawings and lack of electrical contractor, electrical field engineer reviewing existing drawings to prioritize drawings delivery and cable routing..

- Start- up Complete and Ready to Export Power (5%)

Dec 11, 2010 (*) will issue new dates after acceptance or rejection of CO

The dates (*) will be revised as soon as the schedule review is complete and a history is trend is available.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Early  2011* expect slippage

- Unit 200 – 7FA

Early  2011

- CRITICAL AREAS OF CONCERN:

  - Crane move for 7FA generator This will be a total of four  week delay with associated cost exceeding $100K

  - Building design.  Three engineers have reviewed building design, is not suitable.  Need the designer to come to site sit with Sidor and resolve this or Sidor will require modifications to buildings which will be back charged.  Will prepare a notice of back charge to building provider.

  - Installed Site construction power, must check secondary side after stabbing fuses.  Will test tomorrow after installing another ground rod.  Lack of generators and light plants are now a cost to Sidor, they are not accepting temp power even though they inspected prior to shut down to connect.  Punch list cleared no power.

  - Need to assure the 7FA has all materials, contractor support, and resources from PES to meet or shorten the schedule.  Cost for GE TA is 25K per week.  De-mobbed GE after setting Generator.

  - SAFETY:

    - Inclement weather, open excavations, night work with lights

    - Spotters for equipment operators

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Substation Foundations 7FA ISO phase 7FA Generator Breaker(GA#31 7FA FG Heater | TBD |  |  |
| 7FA Fin Fan Fdn | 5 August, 10 |  |  |
| U/G piping | 5May10 | 28May10 | Prepared dwgs in field |
| Design essentially complete | 31 May | No forecast date | No forecast date |

11; Pictures

Photo 1: 7FA site

Photo 2: Compressor and tanks foundation excavations and backfill