CVG SIDOR POWER PROJECT SITE “B”

DATE: 06 May 2010, Thursday PROJECT #: 410-3203 SITE MANAGER: Cole Franklin

TEMPERATURE:  88 F

RANGE: 73 to 90

SITE CONDITIONS: Cloudy and a Light Breeze

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Projectl Manager (A&B)

Cole Franklin - Site Manager

Ted York - Const Manager

Robert James - Safety Mgr (R&R)

Melinda Siros - Doc Control

Dennis Maloney - T/O Coordinator

Ysrin Gomez – Local Safety

Jason Bird - TA/7EA (A&B)

Hal Schulmeyer - Civil Supv

Edward Dubois – QA/QC (A&B)

MATERIAL SUPPORT:

Paul Oliva - Materials                                  Herman Floras – Materials

ADMIN SUPPORT:

Daniel Febres – Logistics

Paulo Gomez - Admin

Patricia Munos - Admin

Skeila Garcia - Translator

Mark Hanks - Electrical Supt

Rafael Soriano - QA/QC (A&B)

Kyle Roskan - Civil Supt

Keith McMurray - Scheduler

Felix Martinez - QA/QC (A&B)

SUBCONTRACTOR PERSONNEL:

General Superintendant        1

Foremen			   2

Electricians                            8

Operators                              4                         Surveyor                                0

Carpenters                           14                          Surveyor Helper                    0

Oiler Helper                           1

Crane Operator                     0                           Laborers                                4

Truck Drivers                         3

Concrete Finishers		   0

Oilers                                     1

Plumbers                               8                        Iron Workers			  14

Helpers                                  2

Welders                                 1			Total:				  63

- GENERAL ITEMS:

  - Luis Acevedo from IDG stated in the meeting today that he is unable to provide any forecast dates at this time do to a redesign of the site which is in process. We are getting close to a work stoppage due to the lack of IFC design drawings. We are in discussions with EDG on this issue.

  - Safety issues are also covered with the contractor in the bi-weekly meeting.

  - GE TA is scheduled to arrive at site on 5-17-10 to perform inventory on 7FA. Currently no bill of material exists on site.

  - Do to the lack of released IFC designs we’ll be running out of work for the contractor. We continue expediting the design drawings.

- CLIENT ISSUES/CONCERN:

  - Progress on Foundation 7EA & 7FA.

  - Underground piping and duct bank drawings scheduled for review 31 Mar 10.

  - Waiting on trash bins from Sidor for site lay down area. We are going to discuss this with Sidor.

  - Sidor is excavating potable water line and preparing to run it to the site tie-in point. Water line continues to leak.

  - Christoph is preparing a drawing showing locations for potable water and fire water tie-in points.

- CIVIL:

  - Coinserman, Ca subcontractor has trailers set on location, is trimming out trailers.

- CONCRETE FOUNDATIONS:

  - Continued installation of rebar and forms for 7EA foundation.

  - Continuing installation of embedded conduits for 7EA foundation.

  - Continued installing drain lines for 7EA foundation. Provided copies of welding information in bi-weekly meeting today. Pro Energy requested numbers be added to the weld map and to x-ray a weld to provide qualification for the welder.

  - Contractor suspended work on 7FA foundation due to commercial issues with PES.

  - Completed installation of structural fill for Treated Fuel Tank.

- MECHANICAL:

  - Prepared a sketch for the 7EA generator replacement jib base plate that was damaged during unit disassembly prior to shipping to site. Sketch will be sent to Tom Koontz to have a replacement plate fabricated and shipped to site.

  - Making arrangements to adjust 7EA generator to allow removal of damaged jib plate.

- PIPING:

- ELECTRICAL:

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS: - Waiting on delivery of replacement 7EA Unisorb base plates and pre-pour items. Plant “B” logistics is handling the shipping. Flight was cancelled in Miami and logistics is working on a replacement flight. - Waiting on welding procedures from Consorcio Megavatio for 7EA stack repairs. Provided company name that can help them assemble a QA plan and welding procedures. They stated in the biweekly meeting yesterday that they would put them together. Forecast 5-14-2010 for submittal. - Waiting on estimates from Consorcio Megavatio for balance of foundation installations. Forecast 5-8-2010 - The internet provider is scheduled to arrive on site tomorrow 5-7-10.

- CRITICAL AREAS OF CONCERN: Consorcio Megavatio supended work on the site except for 7EA and structural fill on Treated Fuel Tank until commercial issues with them are resolved.

  - SAFETY:

    - Consorcio Megavatio will install a bulletin board on site. Forecast 5-14-2010.

    - Weekly safety meetings with Sidor, Concorcio and Pro Energy are scheduled for every Tuesday at 1000 hours at the Plant “A” contractor’s office.

    - Site safety meetings are scheduled for every Monday at 0700 hours at the Plant “A” contractor’s office.

  - OUTSTANDING DRAWINGS:

    - GA, plot plans and foundation drawings all need to be on the same foot print.

    - Grounding grid. Forecast 5-4-2010

    - Duct Bank. Forecast 5-11-2010

    - Underground piping. Forecast 5-5-2010

    - Storm Drain. Forecast 5-12-10

    - 7FA foundations Forecast. 5-11-2010

    - 7FA GSU foundation detailed drawings.

    - Gas Compressor detailed drawings.

    - Balance of foundation details. 5-25 -2010

Note: Email sent by Cole Franklin to Mike Holland on 4-30-10 regarding priorities and needs. Luis Acevedo forwarded email from Mike Holland with forecast dates and items requiring equipment information.

  - ISSUED DRAWINGS:

    - 0919-50-011-0 Plant B Line List

- PICTURES:

Picture 1: Continuing on 7EA Foundation.

Picture 2: Preparing Supports for 7EA Embeds and Anchors.

Picture 3: Trimming Out Trailers for Dust and Weather.

Picture 4: Continuing Installation of Structural Fill for Treated Fuel Tank Foundation.