CVG SIDOR POWER PROJECT SITE “B”

DATE: 07 May 2010, Friday PROJECT #: 410-3203 SITE MANAGER: Cole Franklin

TEMPERATURE:  84 F

RANGE: 75 to 92

SITE CONDITIONS: Partly Cloudy and a Light Breeze

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Projectl Manager (A&B)

Cole Franklin - Site Manager

Ted York - Const Manager

Robert James - Safety Mgr (R&R)

Melinda Siros - Doc Control

Dennis Maloney - T/O Coordinator

Ysrin Gomez – Local Safety

Jason Bird - TA/7EA (A&B)

Hal Schulmeyer - Civil Supv

Edward Dubois – QA/QC (A&B)

MATERIAL SUPPORT:

Paul Oliva – Materials (R&R)                                  Herman Floras – Materials

ADMIN SUPPORT:

Daniel Febres – Logistics

Paulo Gomez - Admin

Patricia Munos - Admin

Skeila Garcia - Translator

Mark Hanks - Electrical Supt

Rafael Soriano - QA/QC (A&B)

Kyle Roskan - Civil Supt

Keith McMurray - Scheduler

Felix Martinez - QA/QC (A&B)

SUBCONTRACTOR PERSONNEL:

General Superintendant        1

Foremen			   2

Electricians                            2

Operators                              0                         Surveyor                                1

Carpenters                           14                          Surveyor Helper                    2

Oiler Helper                           1

Crane Operator                     0                           Laborers                                4

Truck Drivers                         0

Concrete Finishers		   0

Oilers                                     1

Plumbers                               2                        Iron Workers			  14

Helpers                                  2

Welders                                 1			Total:				  47

- GENERAL ITEMS:

  - We are getting close to a work stoppage due to the lack of IFC design drawings. We are in discussions with EDG on this issue.

  - Safety issues are also covered with the contractor in the bi-weekly meeting.

  - GE TA is scheduled to arrive at site on 5-17-10 to perform inventory on 7FA. Currently no bill of material exists on site.

  - Do to the lack of released IFC designs we’ll be running out of work for the contractor. We continue expediting the design drawings.

  - Union for Sidor had a strike today which kept PES personnel inside the office and at the sites during the demonstrations.

  - No cement available to make sufficient concrete for Saturday 8 May 10 pour of the mud mat for the 7FA. Concrete will not be available until 10 May 10.

- CLIENT ISSUES/CONCERN:

  - Progress on Foundation 7EA and 7FA.

  - Underground piping and duct bank drawings scheduled for review 31 Mar 10.

  - Waiting on trash bins from Sidor for site lay down area. We are going to discuss this with Sidor.

  - Christoph (Sidor) is preparing a drawing showing locations for potable water and fire water tie-in points.

- CIVIL:

  - Coinserman, Ca subcontractor has trailers set on location, ready for A/C, furniture and cleaning.

- CONCRETE FOUNDATIONS:

  - Continued installation of rebar and forms for 7EA foundation.

  - Continued installation of embedded conduits for 7EA foundation.

  - Began installing anchor bolts for 7EA foundation.

  - Continued installing drain lines for 7EA foundation. Provided copies of welding information in bi-weekly meeting, 5-06-10. Pro Energy requested weld numbers to be added to the weld map and to x-ray a weld to provide qualification for the welder.

  - Contractor has resumed work on 7FA and will begin to remobilize personnel and equipment on Monday.

  - Concrete is not available till Monday 10 May 10. Postponed pour till then.

- MECHANICAL:

  - Verifying sketch for the 7EA generator replacement jib base plate and adding some notes for clarifications. Sketch will be sent to Tom Koontz to have a replacement plate fabricated and shipped to site.

  - Making arrangements to adjust 7EA generator to allow removal of damaged jib plate.

- PIPING:

- ELECTRICAL:

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS: - Waiting on delivery of replacement 7EA Unisorb base plates and pre-pour items. Plant “B” logistics is handling the shipping. 5-7-10 received email that there is a discrepancy in the paper work and being held in customs. - Waiting on welding procedures from Consorcio Megavatio for 7EA stack repairs. Provided company name that can help them assemble a QA plan and welding procedures. They stated in the biweekly meeting yesterday that they would put them together. Forecast 5-14-2010 for submittal. - Waiting on estimates from Consorcio Megavatio for balance of foundation installations. Forecast 5-8-2010 - The internet provider is scheduled to arrive 5-7-10.

- CRITICAL AREAS OF CONCERN:

- Consorcio Megavatio has resumed work on the 7FA. They will begin remobilizing personnel and equipment on Monday.

- We are getting close to a work stoppage due to the lack of IFC design drawings. We are in discussions with EDG on this issue.

  - SAFETY:

    - Consorcio Megavatio will install a bulletin board on site. Forecast 5-14-2010.

    - Weekly safety meetings with Sidor, Concorcio and Pro Energy are scheduled for every Tuesday at 1000 hours at the Plant “A” contractor’s office.

    - Site safety meetings are scheduled for every Monday at 0700 hours at the Plant “A” contractor’s office.

  - OUTSTANDING DRAWINGS:

    - GA, plot plans and foundation drawings all need to be on the same foot print.

    - Duct Bank. Forecast 5-11-2010

    - Underground piping. Forecast 5-5-2010 slipped

    - Storm Drain. Forecast 5-12-10

    - 7FA foundations Forecast. 5-11-2010

    - 7FA GSU foundation detailed drawings.

    - Gas Compressor detailed drawings.

    - Balance of foundation details. 5-25 -2010

Note: Email sent by Cole Franklin to Mike Holland on 4-30-10 regarding priorities and needs. Luis Acevedo forwarded email from Mike Holland with forecast dates and items requiring equipment information. Cole is responding with the pending issues on issued and drawings shown as issued, but not received at site.

  - ISSUED DRAWINGS:

- Grounding Plan ( Drawings are under review and PES has some issues with designs)

- PICTURES:

Picture 1: Continuing on 7EA Foundation.

Picture 2: Installing 7EA Anchors.

Picture 3: Installing 7EA Conduits, Anchors and Drain Lines.

Picture 4: Structural Fill for Treated Fuel Tank Foundation Completed Yesterday.

Picture 5: Installing Forms for Mud Mat for 7FA.