CVG SIDOR POWER PROJECT SITE “B”

DATE: 11 May 2010, Tuesday PROJECT #: 410-3203 SITE MANAGER: Cole Franklin

TEMPERATURE:  88 F

RANGE: 75 to 89

SITE CONDITIONS: Scattered Clouds in the Morning and Mostly Clouds by Noon

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Project Manager (A&B)

Cole Franklin - Site Manager

Ted York - Const Manager

Melinda Siros - Doc Control

Dennis Maloney - T/O Coord & Safety

Ysrin Gomez – Local Safety

Jason Bird - TA/7EA (A&B)

Hal Schulmeyer - Civil Supv

Edward Dubois – QA/QC (A&B)

MATERIAL SUPPORT:

Jose Angel – Materials

ADMIN SUPPORT:

Daniel Febres – Logistics

Paulo Gomez - Admin

Patricia Munos - Admin

Skeila Garcia - Translator

Mark Hanks - Electrical Supt

Rafael Soriano - QA/QC (A&B)

Kyle Roskan - Civil Supt

Keith McMurray - Scheduler

Felix Martinez - QA/QC (A&B)

SUBCONTRACTOR PERSONNEL:

General Superintendant        1

Foremen			   2

Electricians                            0

Operators                              0                         Surveyor                                1

Carpenters                           12                          Surveyor Helper                    2

Oiler Helper                           0

Crane Operator                     0                           Laborers                                4

Truck Drivers                         0

Concrete Finishers		   0

Oilers                                     0

Plumbers                               2                        Iron Workers			  12

Helpers                                  2

Welders                                 1			Total:				  39

- GENERAL ITEMS:

  - Luis Acevedo from IDG stated in the meeting, 5-3-10, that he is unable to provide any forecast dates at this time do to a redesign of the site which is in process. We are getting close to a work stoppage due to the lack of IFC design drawings. We are in discussions with EDG on this issue.

  - Safety issues are also covered with the contractor in the bi-weekly meeting.

  - 7FA inventory is being performed with GE TA.

- CLIENT ISSUES/CONCERN:

  - Progress on Foundation 7EA and 7FA.

  - Underground piping and duct bank drawings scheduled for review 31 Mar 10.

  - Waiting on trash bins from Sidor for site lay down area. We are going to discuss this with Sidor.

  - Christoph is preparing a drawing showing locations for potable water and fire water tie-in points.

- CIVIL:

  - Subcontractors are sealing trailers, installing power, furniture, A/C’s. Sewage treatment for site trailers is wired and piped ready for start up.

- CONCRETE FOUNDATIONS:

  - Continued installation of rebar and forms for 7EA foundation.

  - Continued installation of anchor bolts for 7EA foundation.

  - Pro Energy requested weld numbers to be added to the weld map for 7EA drain lines, 5-6-10.

  - Concrete pour for 7FA mud mat was completed around 2200 hours last night.

  - Replacement 7EA Unisorb base plates are being held by customs due to a discrepancy in shipping documents, 5-7-10.

  - Completed installation of rebar for center pedestal for Treated Fuel Tank. Completed pour of pedestal.

  - Receiving rebar for 7FA foundation.

- MECHANICAL:

  - Completed sketch for the 7EA generator replacement jib base plate, 5-8-10. Emailed sketch to Tom Koontz to have a replacement plate fabricated and shipped to site, 5-08-10.

  - Adjusting 7EA generator to allow removal of damaged jib plate is setup for 5-12-10 with Sidor.

- PIPING:

- ELECTRICAL:

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS: - Waiting on welding procedures from Consorcio Megavatio for 7EA stack repairs. Provided company name that can help them assemble a QA plan and welding procedures. They stated in the biweekly meeting yesterday that they would put them together. Forecast 5-14-10 for submittal. - Waiting on estimates from Consorcio Megavatio for balance of foundation installations. Forecast 5-8-10. No new forecast date in today’s meeting. The superintendent is working with the office to produce estimates. - Consorcio Megavatio provided pull box detail for duct banks for engineering approval to enable precast in order to expedite the project. - The internet provider is scheduled to begin installation on 5-11-10 for site trailers.

- CRITICAL AREAS OF CONCERN: Changes in designs are impacting project progress/completion. Shortage of cement is affecting the scheduling of foundations. Consortium stated in today’s meeting that they cannot start a second shift due to the lack of approved/complete drawings which would support the shift. Once there are sufficient approved/complete drawings they can start a second shift the following week.

  - SAFETY:

    - Consorcio Megavatio will install a bulletin board on site. Forecast 5-14-2010.

    - Weekly safety meetings with Sidor, Concorcio and Pro Energy are scheduled for every Tuesday at 1000 hours at the Plant “A” contractor’s office.

    - Site safety meetings are scheduled for every Monday at 0700 hours at the Plant “A” contractor’s office.

  - OUTSTANDING DRAWINGS:

    - Plot plans and foundation drawings all need to be on the same foot print.

    - Duct Bank. Forecast 5-11-2010

    - Underground piping. Forecast 5-5-2010. Received 5-11-10; performed a review which reveiled missing drawings, BOP listed as 156’( Example), pipes ending no where, review blocks incomplete and Raw Water being routed to equipment in the site. EDG is reviewing.

    - Storm Drain. Forecast 5-12-10

    - 7FA foundations Forecast. 5-11-2010

    - 7FA GSU foundation detailed drawings.

    - Gas Compressor detailed drawings.

    - Balance of foundation details. 5-25 -2010

    - Informed EDG that the water seal shown on the foundation drawings is not available here in country. They are reviewing this issue.

    - Grounding Plan ( Drawings are under review and PES has some issues and concerns with the designs).

Note: Email sent by Cole Franklin to Mike Holland on 4-30-10 regarding priorities and needs. Luis Acevedo forwarded email from Mike Holland with forecast dates and items requiring equipment information. Pro Energy is reviewing the EDG drawing log with what has been issued to the site. Results have been issued.

  - ISSUED DRAWINGS:

    - General Arrangement

    - Under Ground Piping. Performed a review which reveiled missing drawings, BOP listed as 156’( Example), pipes ending no where, review blocks incomplete and Raw Water being routed to equipment in the site. EDG on site is reviewing red lines.

    - Sketch for Man Hole and Hand Hole Location for Duct Bank

- PICTURES:

Picture 1: Installing Anchor Bolts for 7EA Foundation.

Picture 2: Completed Mud Mat for 7FA Foundation.

Picture 3: Sewage Treatment Wired and Plumbed for Site Trailers.

Picture 4: Installing A/C’s for Site Trailers.

Picture 5: Excavation for Power to Trailer.

Picture 6: Installing Internet at the Site Trailers.

Picture 7: Pouring the Center Pedestal for Treated Fuel Tank.