CVG SIDOR POWER PROJECT SITE “A”

DATE:  12 May 2010, Monday

PROJECT #: 410-3202

LOCATION: SIDOR Industrial Area, Puerto Ordaz, Venezuela

SITE MANAGER: Patrick Melody

TEMPERATURE:  88 F

RANGE: 75 to 95 F

SITE CONDITIONS: Rain storm @ approximately 12:00

PERSONNEL ON SITE:

| Lugo Bill | Project Director | Jason Bird | Tech Adviser 7EA |
| --- | --- | --- | --- |
| Melody Patrick | Site Manager |  |  |
| Sewell David | Const. Manager | Meyer Daniel | Material Support |
| Blacke Edward | Safety Manager | Horn Ryan | Tool Room Super. |
|  |  | Little John | Material Coordinator |
| Bretherick Teresa | Scheduler | Daniels Julio | Tool Room (Local) |
|  |  | Izquierdo Weiser | Mat'l. Handler (Local) |
|  |  | Lopez Juan Carlos | Mat'l. Handler (Local) |
| Siros James | Mech. Supt. | Ortega Ramon | Tool Room (Local) |
| Archuleta Pete | Piping Supt. |  |  |
| Riley Jasper | Electrical Supt |  |  |
| Herasimchuk Michael | I & C Supt. | Leccia Karina | Admin Assist |
| Soriano Rafael | QA/QC Manager | Mendez Kenia | Admin Assist |
| Thomas Hankins | QA/QC Manager | Zambrano Natalia | Translator |
| Contreras Wilson | Mechanical Supt |  |  |

SUBCONTRACTOR PERSONNEL:

Operators                            11                               Mechanical Assit.                   4

Carpenter                            29                               Electrician                              3

Laborers                              38                               Helper                                  57

Truck Driver                           4                               Operator Crane                     2

Welders                                 5                               Plumber                                 2

Oilers                                    1                               Mechanic Heavy                    1

Master Operator                    4                               Master Mechanic                   1

Survey Assistant                   2                               Concrete Finsher                 14

Surveyor                               2                                Warehouse  Assist                2

Oiler                                      1                                Total                                 184

- GENERAL ITEMS

    - Design and procurement for the project needs to be completed as soon as possible to support current project schedule.

- CLIENT ISSUES/CONCERNS:

    - Location of existing gas line between 7EA and Control Building remains undeterminable after test pitting.

    - Relocation of overhead lines at fuel oil tank area expected to be complete within the next 7 days. Overhead lines are preventing excavation of Raw Water Tank and Fuel Storage Tank..

    - Fire line connection and design meeting was held with Sidor. Sidor has been requested to provide complete Water Flow Test Data including Static/Residual pressure. Information is required to complete design and procurement activities.

    - Septagon, pre-engineered building supplier, to revise foundation drawings to address Sidor’s concerns. This drawing is needed urgently because this building is in the critical path.

- CIVIL:

    - Place concrete cable rack foundations

    - Install conduit 15 kV Breaker MH 6

    - Excavate fuel storage tank

    - Form/Rebar GT 300 GSU blast wall

    - Excavate duct bank MH 8 to MH 9

    - Install Engineered Fill at Demin Water Tank

    - Excavate pipe rack at GT 200

- CONCRETE FOUNDATIONS:

    - Pipe rack Foundation piers  concrete placement

- MECHANICAL:

    - GT 100 Clean Generator Oil Tank

    - GT 200 Install and torque bolts for plenums and roof skids.

    - GT 300 Align exhaust stack base for welding

    - GT 300 Exhaust stack weld prep

    - GT 300 Grout Fixators

    - GT 300 Prep weather hoods for filter house

    - Fabricate pipe for fire line loop

    - GT 300 Place generator adjacent to foundation

    - GT 300 Cleaning transition duct for filter house

    - GT 300 Remove /clean generator sole plates

    - Clean turbine sole plate

- ELECTRICAL:

    - Install conduit in duct banks

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS:

    - CPS Schedule development on going. First draft being reviewed by the team.

- CRITICAL AREAS OF CONCERN:

Design and procurement for the project needs to be completed to as soon as possible to support current project schedule.

    - SAFETY:

      - Develop JSA as needed

      - Inspection of subcontractor power tools.

      - Inspection of motorized equipment prior to usage.

    - OUTSTANDING DRAWINGS:

9.1.2.1	Grounding grid

      - Coordinated underground drawing

      - Switch yard foundations and related duct banks

      - Cable rack foundation drawings

      - Design drawings need to be issued

      - Utility Bldg. Housekeeping pads for electrical equipment.

    - DRAWINGS ISSUED:

Approximately 60 IFC drawings were issued.

8	PICTURES:

GT 300 Grouting Fixators

GT 300 Generator

Demin Water Tank Engineered Back Fill

GT 300 Stack Weld Prep