# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 23 July 2010, Friday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin (R&R until July 30th, 2010)

TEMPERATURE:  85 F

RANGE: 76 to 88

SITE CONDITIONS: mostly cloudy – Rain late afternoon

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Project Mgr (A&B)

Cole Franklin - Site Manager  (R&R)

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Unfilled mechanical/piping (local ASAP)

Mark Hanks - Electrical Supt (A&B)

Unfilled - elect. field eng.(local ASAP)

Kyle Roskam - Civil Supt (A&B)

Felix Martinez-QA/QC (A&B)

Unfilled QA/QC supervisor (local ASAP)

Melinda Siros for unfilled – Document control  (asap)

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Paul Olivo – Materials

– tool room (Local)

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila Garcia – Translator/Doc Control (Local)

Richard Gaines – EDGI electrical (A&B)

SUBCONTRACTOR PERSONNEL: Concorcio Megavatio

General Superintendant		1

Safety					1

Foremen				3

Electricians				0

Operators				0                      Surveyor				1

Carpenters				7    Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				4

Truck Drivers				0

Concrete Finishers			0

Oilers					0

Plumbers				0                        Iron Workers				10

Helpers				4

Welders				2

Total:					35

Contractor PERSONNEL:

ISI

General Superintendant		0

Safety					1

Foremen				1

Operators				1

Oiler Helper				0

Crane Operator			1                           Laborers				0

Truck Drivers				1

Mechanic	      			6

Helpers				6

Pipe fitter

Welders				2

- GENERAL ITEMS

  - Contacted a pressure grouting company they came to site.  He will prepare a quote for the pressure grouting by early next week.  We need to order the grout from US, not available here.  We’ll proceed to prepare a draft order from states.

  - Little work on 7FA foundation, the anchor bolts shipped to freight forwarder today.  Air freight confirmed for 7/24/10 departure.

  - We issued the PO for signature and hopefully will start excavation for duct bank.  We are scheduling to start working next week.  Delivered by transmittal drawing from Sidor for the pull boxes (manholes), and all drawings issued or revised since original meetings.  There is a significant delta, will start work on a unit cost basis.

  - Proposal for modifying sea containers for lay down area office, temperature controlled storage and running power to area.  PO issued

  - Prepared a quote for a change order, but cannot issue without knowing which of the three locations will be used.  If no super lift kit will use two of the three locations.

  - We will need duct bank details for the area immediately adjacent to GSU 100 when we start excavation for the GSU after crane moves, must pour duct bank area before GSU.  Sent RFI Sidor B 0002 no response again today; HV PES is also working on the duct banks on the side of the switchyard.

  - GSU embeds mechanical contractor will fabricate them at site. We’ll follow u with ISI on the status of these.

- CLIENT ISSUES/CONCERN:

  - The client was made aware that type II concrete is necessary for 7FA foundation and adequate equipment plus adequate delivery rate is essential.  Client has made no promises regarding availability of type II cement.  Sent EDGI RFI Sidor B 0003.

  - Meeting held at site with Sidor engineering, and PES regarding Fuel oil tank movement.  We prepared a CO for this submitted to Derwick.

  - Prepared a list of all needed from Sidor to accelerate the project.

- CIVIL:

  - Oily water separator form work ongoing.

  - Installing gen enclosure 7EA.

  - PEECC, ISI manufacturing embeds.  Hilti RE500 onsite for embedding the plates. We’ll follow u with ISI on the status of these.

  - Staked location of WW Tank Foundation. Coordinate issues, communicating with Engineering for solution.

  - Lack of resolution for Treated Fuel Oil Tank location, awaiting CO. CO will be issued to Derwick next Monday.

- CONCRETE FOUNDATIONS:

  - Work on the 7FA main slab halted, finished stack foundations, expect bolts.

  - 7FA anchor bolts, released for shipment, expected on site 26, needed at site 20 July to meet present schedule.

  - PEECC embeds to be built by ISI (mechanical contractor)

  - Crane moved to allow start of GSU excavation.  Still waiting for a response to RFI Sidor B 0002 from EDGI and for the switchyard underground design from PES HV.  Need info on conduits and elevations for duct bank adjacent to GSU.

- MECHANICAL:

  - Issued PO for start of 7EA stack repairs and erection.

  - Required back fill under crane is completed.  Will possibly set first stack section tomorrow.

  - Started ISI with 12 people, installing gen enclosure

- PIPING:

  - Issued PO for piping to ISI, will mobilize this week, slipped to Monday for welding certification

  - Will start ISI on prefab of U/G piping.  Will double joint 10” RW piping

- ELECTRICAL:

  - Loaned 5800 linear feet of conduit to Site A.  They will order to replace it, will need it within 1 week.

  - Coinserma civil contractor for duct bank will require a large amount of PES time to supervise this work. A new electrical local field engineer will start supporting this effort next Monday.  There is a delta between quote and present scope of work will start Monday with excavation.

  - The underground piping and duct bank is now critical path and is driving the schedule, can afford no more delays.

  - Need to review cathodic protection general specifications; We sent Luis Acevedo a request for advance copy, he advises it is not available.  Issued PO for U/G pipe Friday past I understand, we can get specs shortly.

  - Need duct bank information adjacent to GSU RFI issued no response today.

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Contractor increases manpower to work in all areas

- Contractor works two shifts or a 12 hours shift

- The Underground and duct bank is started week of 7 June 19 July and does not slip more

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (50%)

Complete

- Gas Turbines on Foundation (10%)

July 19, 2010 this has slipped for 7FA due to shortage of anchors, we must come up with an incentive to contractor to accelerate the schedule and we must receive the materials for the foundations.  We think the extension as of now is 3 weeks or Sep 5, 2010 for 7FA

- Civil Foundations Complete (25%)

Sep 15, 2010 (*) do not have all drawings for foundations RFI 0006 issued to EDGI for forecast dates.  We will start duct bank excavation next Monday July 26th.  We expect at least 3 weeks delay, reviewing schedule to attempt to cut time see section 9.

- Electrical/Mechanical Complete (10%)

Dec 3, 2010 (*) expect at least 3 weeks due to lack of drawings and lack of electrical contractor

- Start- up Complete and Ready to Export Power (5%)

Dec 11, 2010 (*) see above expect a revised schedule week end

The dates (*) will be revised as soon as the schedule review is complete. We expect this review is completed early next week.

9.3 Ready for Start-up Dates

- Unit 100 – 7EA

Nov 29, 2010

- Unit 200 – 7FA

Dec 11, 2010

- CRITICAL AREAS OF CONCERN:

  - Lack of materials (anchor bolts 7FA shipped to freight forwarder today) , embed plates 7EA PEECC

  - Changes in designs are impacting project progress/completion.   Need drawings for all foundation and updated GA to meet progress milestone.

  - Need finalized design or if that cannot be completed, need to include all equipment on GA and freeze the design with Sidor approval.

  - Shortage of cement is affecting the scheduling of foundations.

  - Need to Issue RFI for Building drawings series 30 issued 20 July Sidor B RFI 0001.

  - Material deliveries and the trickle down caused by commercial issues seriously retard our ability to execute schedule.  Received a partial list of materials on first ship, to arrive on or about 5 Aug, should be available no more than 1 week after.

  - SAFETY:

    - Concorcio Megavatio reported job site information board was assembled and ready to bring to site for installation.   Pending resolution of commercial issues.

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| GSU 7EA | 15May10 | 25May10 | Need duct bank detail adjacent to GSU |
| Balance of FDN drawings | 25May10 | 3Jun10 | No date, delivery impacts payment milestones |
| Treated Fuel Tank updated drawings | 29May10 | 1Jun10 | prepared quote for moving tank pending |
| U/G piping | 5May10 | 28May10 | Comments pending |
| GSU 7FA | 21May10 | 2 Jun10 | Not critical |
| Design essentially complete | 31 May | No forecast date | No forecast date |

  - ISSUED DRAWINGS:

11. PICTURES:

Oily Water Separator form work

Site B view from office