|  |
| --- |
| **CVG SIDOR POWER PROJECT SITE “B”**  **PROJECT: 410-3203** |
| **DATE: 27 April 2010 Tuesday** |

**TEMPERATURE: 95 F RANGE: 75 to 95**

**SITE CONDITIONS: Partly Cloudy and Breezy**

**PERSONNEL ON SITE:**

William Lugo - Project Manager Hal Schulmeyer - Civil Supt

Robert James - Safety Mgr Gene Phillips - PE Civil - Wallace

Cole Franklin - Site Manager Melinda Siros - Doc Control

Ted York - Const Manager Dennis Maloney - T/O Coordinator

Daniel Febres – Logistics

Keith McMurray - Scheduler

Felix Martinez - QA/QC Mark Hanks - Electrical Supt

Rafael Soriano - QA/QC Kyle Roskan - Civil Supt

Paul Oliva - Materials Wilson Confrera - Materials

Ysrin Gomez - Safety

Jason Bird - TA/7EA

**SUBCONTRACTOR PERSONNEL:**

General Superintendant 1

Foremen 1

Electricians 0

Operators 3 Surveyor 1

Carpenters 14 Surveyor Helper 2

Oiler Helper 1

Crane Operator 0 Laborers 4

Truck Drivers 1 Concrete Finishers 0

Oilers 1

Plumbers 0 Iron Workers 14

Helpers 0

Welders 0

**TOTAL:**  43

1. **CLIENT ISSUES/CONCERN:** 
   1. Progress Foundation 7EA & & 7FA
   2. Weather protection for material and equipment in lay down yard Sidor provided Tarps, not installed.
   3. Geo tech report addendum for 7FA foundations.
   4. Underground piping and duct bank drawings scheduled for review 31 Mar 10.
   5. Running Fire Water and Potable Water to site per red lined drawing.
2. **CRITICAL AREAS OF CONCERN:**
   1. **SAFETY:**
      1. Trash Bins and Barrels to be supplied by Sidor.
      2. Consorcio Megavatio needs to provide a first a kit.
      3. Pro Energy shipped two medical kits for use at site offices.
      4. Consorcio Megavatio is going to setup and First Aid office on site.
      5. No safety person on site for Consorcio Megavatio.
      6. No emergency shower or eye wash station is on site for Consorcio Megavatio.
      7. Received a copy of the accident report from April 21, 2010 from Consorcio Megavatio.
      8. Need a job site bulletin board by Consorcio Megavatio.
      9. Emergency assembly area needs to be established by Consorcio Megavatio.
      10. Need a hand washing facility for workers by Consorcio Megavatio.
      11. Equipment needs to be marked with the PPE requirements for operation by Consorcio Megavatio.

Note: Consorcio Megavatio issues were covered in meeting today.

* 1. **OUTSTANDING DRAWINGS:** 
     1. Grounding grid
     2. Duct Bank
     3. Underground piping / storm drain system
     4. 7FA foundations
     5. Balance of foundation details

|  |
| --- |
| 1. **SCHEDULED ITEMS:**    1. Mike Curley with EDG is going to take look at the piping materials and quantities we received for review since we have no design to help verify the quantities are not excessive.    2. Had meeting today with Sidor, Geo Tech Engineer and Consorcio Megavatio to review Geo tech report. Explanation by Geo Tech Engineer clarified issues. Meeting minutes were forwarded to GDI engineering for review and concurrence.    3. Inventory of 7FA material and equipment is in process. Waiting for forecast date of GE Tech to do inventory. Currently no bill of material exists on site.    4. Waiting on delivery of replacement 7EA Unisorb base plates and pre-pour items. Plant “B” logistics is handling the shipping.    5. Still waiting on welding procedures from Consorcio Megavatio for 7EA stack repairs.    6. Waiting on estimates from Consorcio Megavatio for balance of foundation installations.    7. Sidor is allowing potable water for trailers to be ran from the existing plant just north of the trailer location to the plant south side of the trailers.    8. Waiting on review by Christoph of Sidor for Fire Water tie-ins, Potable Water tie-ins and depths of duct banks and utilities for routing of storm drains.    9. Waiting on reply to site letter issued to Consorcio Megavatio about outstanding issues.    10. Discussed concerns of 7FA foundation infringement into the future HRSG foundation in engineering phone call today. They replied it is not an issue. Construction expressed their concerns if the HRSG is added. |

1. **CIVIL:**
   1. Continued installation of rebar for 7EA.
   2. Completed excavation of Oily Water Separator. Received information from EDG that it is being relocated so hole will be filled.
   3. Five site trailers/office was delivered today. Coinserman, Ca subcontractor poured half of the mud mat and cut in road from existing to the lay down area. Began installation of gravel on road. Marteniz with Sidor said he wanted the trailers set in place using a crane instead of a forklift. We are discussing availability of crane and rigging with Sidor.
2. **MECHANICAL:**
3. **ELECTRICAL:**
4. **INSTRUMENTATION AND CONTROLS:**
5. **PICTURES:**



**Picture 1: Installing Rebar for 7EA.**



**Picture 2: Five Site Trailers Were Delivered to Plant B.**



**Picture 3: Pouring Mud Mat for Site Trailers.**



**Picture 4: Preparing Road for Trailers and Lay Down Area.**



**Picture 5: Road to Lay Down Area.**