# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 3 June 2010, Wednesday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  86 F

RANGE: 77 to 93

SITE CONDITIONS: Cool morning, overcast

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Project Mgr (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Mark Hanks - Electrical Supt (travel R&R)

Kyle Roskam - Civil Supt

MATERIAL SUPPORT:

Jose Angel Gonzales – Materials (Local)

Paul Oliva – Materials

ADMIN SUPPORT:

Daniel Febres – Logistics (Local) medical leave

Paulo Gómez – Admin (Local)

Patricia Munos – Admin (Local)

Skeila Garcia – Translator & Doc Control (Local)

SUBCONTRACTOR PERSONNEL:

General Superintendant		1

Foremen				2

Electricians				0

Operators				0                        Surveyor				1

Carpenters				8    Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				3

Truck Drivers				0

Concrete Finishers			0

Oilers					0

Plumbers				0                        Iron Workers				14

Helpers				2

Welders				2

Total:					35

- GENERAL ITEMS:

  - GSU for Site A damaged in transit.  I am informed the GSU for B will be installed in A and the repaired GSU will be delivered to B.

  - The center lines for locating the fixators are being prepared for installation of the fixators.  The fixators are being adjusted in advance of starting the installation.  The fixators will be finished no later than Saturday.

  - Proposal for modifying sea containers for lay down area office, temperature controlled storage and running power to area offer is on hold pending resolution of commercial issues.

  - RFP for trash containers and disposal of trash is prepared pending new quotes, and commercial issue resolution.

  - Site continues a material takeoff of drawings available at site, generated RFP for anchor bolts and RFP for conduit in duct banks.

- CLIENT ISSUES/CONCERN:

  - Progress on Foundation 7FA, and schedule slippage.  Progress overall.

  - Underground piping and duct bank drawings scheduled for review 31 Mar 10. Is late new date for duct bank dwgs 7 June, will discard the sketches and provide IFC drawings. Request for purchase for trash bins for site lay down area and construction site released RFP for delivery dates. Sidor was asked to provide this, but never delivered.

  - Sidor to produce fire water flow rates for Plant B, no forecast date provided.

  - Sidor expressed concern for the drawings review process and the comments getting into the drawings.  We are reviewing drawings for completeness in hopes of forestalling delays

- CIVIL:

  - Concrete issues; requested a meeting with Sidor and both concrete batch plants for planning the 7FA foundation.  The rate and quality of concrete (rejection of trucks) is a major issue for the larger pour.   In contractor’s meeting Sidor requested a pre meeting with contractor and PES to discuss concrete batch plant and concerns for 7FA pour.  No forecast date for mtg, Sidor plans to resolve this issue at a higher level.

- CONCRETE FOUNDATIONS:

4.1 	Work today on the 7FA with small crew of manpower and continue form stripping 7EA.  The work is progressing very slowly due to the lack of manpower and materials.  We have had an apparent one (1) week delay in the past three (3) weeks.

4.2 Installation of  the fixators for 7EA as per current plan will mitigate one week of this delay.

4.2	Contractor agreed to continue with all 7EA equipment including GSU, PEECC, and Stack.  Issues RFP for 7EA anchor bolts, hope to have delivery date tomorrow.

- MECHANICAL:

5.1 	7EA generator replacement jib base plate is being fabricated in Sedalia. Tom Koontz will ship by air freight to site as soon as it is complete. Current forecast is 5-29-10.  This is critical, plan to set equipment next week.  Today received an e-mail indicating delivery next week.

5.2	Requested ISI to provide insurance certifications.  They are non responsive now, possibly due to commercial discussions.

- PIPING:

6.1	Review ongoing of material takeoff for bulk order of piping.

- ELECTRICAL:

  - Started survey for manholes.  Concorcio is worried; they were notified that we are bringing in another contractor for duct bank and misc civil excavations.  They agreed after the discussion to work all 7EA fdns.

  - Will add a lighting breaker panel for office trailers, very concerned for the “piggybacking” of wires into the breaker we installed. On hold awaiting resolution of commercial issues

  - Concorcio gave us a list of materials for the site construction power transformer installation. Sidor (Daniel) called and says PES should provide this material.

  - The drawings for the 7EA (unit 100) GSU are still wrong.  Prepared RFP for embeds for GSU.  We will red line and continue.

  - The sub contractor Coinserma came to site for meetings regarding the duct bank work.  Coinserma says they cannot or will not prepare a fixed price bid against the drawings presently at site.  This has a potential for a delay in start of work.  Drawings are forecast available 7 June

  - The underground piping and duct bank is now critical path and is driving the schedule, can afford no more delays.

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS: 9.1 General Schedule issues The schedule is predicated by the following: Commercial issues are resolved to local purchase materials Contractor increases manpower to work in all areas Contractor works two shifts The Underground and duct bank is started next week and does not slip more Sedalia material delivers are forthcoming to meet demand 9.2 Milestone Payment Estimated Delivery The 7EA is scheduled to be placed on the foundation next week, should conclude installation of CTG Monday of the following week. 9.3 Payment milestones The mechanical complete for Unit 100 (7EA) date is currently

- CRITICAL AREAS OF CONCERN:

  - Sidor provided crane has not mobilized, I understand it takes a week to mobilize.

  - Changes in designs are impacting project progress/completion.

  - Shortage of cement is affecting the scheduling of foundations.

  - Meeting requested with Sidor and both concrete batch plant managers to discuss quality and rate of flow for the concrete for future pours.

  - Duct Bank drawings now forecast for Monday 7Jun10.

  - Underground piping received e-mail today indicating EDGI is awaiting P
ES, sent e-mail to Tom Koonce to attempt to resolve this.

  - Material deliveries and the trickle down caused by commercial issues seriously retard our ability to plan and execute

  - SAFETY:

    - Concorcio Megavatio reported job site information board was assembled and ready to bring to site for installation.   Pending resolution of commercial issues.

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| GSU 7EA | 15May10 | 25May10 | Issued new rev, but still oriented wrong |
| Balance of FDN drawings | 25May10 | 3Jun10 | slipped |
| Treated Fuel Tank updated drawings | 29May10 | 1Jun10 | slipped |
| U/G piping | 5May10 | 28May10 | See item 10.5 |
| GSU 7FA | 21May10 | 2 Jun10 | slipped |
| Duct Bank | Had sketch to use for bid review | 7 June 10 |  |
| Design essentially complete | 31 May | No forecast date |  |

    - A spread sheet of all the pending drawing issues noted here is being consolidated; these issues will be captured for both sites.

    - After review of the duct bank drawings Pro Energy requested EDG assess depth of conduits leaving hand holes, perform an evaluation for areas where load bearing equipment will be set up (cranes, forklifts, etc) over duct banks and if RGS conduit should be used in these areas with steel reinforced cage, The handhold elevation will not cover 4” 36” radius 90 degree turns in conduit.

    - Underground piping. Received an e-mail advising they need information from PES to continue.  Tom Koonce has given info and will provide remaining next week

.

  - ISSUED DRAWINGS:

None received by e-mail today

11. PICTURES:

Photo 1: 7FA crew top rebar installation

Photo 2: installing forms on 7FA after removal from 7EA