CVG SIDOR POWER PROJECT SITE “A”

DATE:  7 May 2010, Friday

PROJECT #: 410-3202

LOCATION: SIDOR Industrial Area, Puerto Ordaz, Venezuela

SITE MANAGER: Patrick Melody

TEMPERATURE:  88 F

RANGE: 75 to 95 F

SITE CONDITIONS: Sunny with Scattered Clouds

PERSONNEL ON SITE:

| Lugo Bill | Project Manager | Jason Bird | Tech Adviser 7EA |
| --- | --- | --- | --- |
| Melody Patrick | Site Manager | Allan Hill | Tech Adviser LM 600 |
| Sewell David | Const. Manager | Meyer Daniel | Material Support |
| Blacke Edward | Safety Manager | Horn Ryan | Tool Room Super. |
| Urbana Diomarys | Local Safety Manager | Little John | Material Coordinator |
| Bretherick Teresa | Scheduler | Daniels Julio | Tool Room (Local) |
| Cornett Clarence | Civil Supt | Izquierdo Weiser | Mat'l. Handler (Local) |
| Kirk Scott | Civil Support | Lopez Juan Carlos | Mat'l. Handler (Local) |
| Siros James | Mech. Supt. | Ortega Ramon | Tool Room (Local) |
| Archuleta Pete | Piping Supt. |  |  |
| Riley Jasper | Electrical Supt | Cornett Elizabeth | Document Control |
| Herasimchuk Michael | I & C Supt. | Leccia Karina | Admin Assist |
| Soriano Rafael | QA/QC Manager | Mendez Kenia | Translator |
| Thomas Hankins | QA/QC Manager | Zambrano Natalia | Translator |
| Contreras Wilson | Mechanical Supv |  |  |

SUBCONTRACTOR PERSONNEL:

Operators                            11                               Mechanical Assit.                   4

Carpenter                            29                               Electrician                              3

Laborers                              38                               Helper                                  57

Truck Driver                           4                               Operator Crane                     2

Welders                                 5                               Plumber                                 2

Oilers                                    1                               Mechanic Heavy                    1

Master Operator                    4                               Master Mechanic                   1

Survey Assistant                   2                               Concrete Finsher                 14

Surveyor                               2                                Warehouse  Assist                2

Oiler                                      1                                Total                                 184

- GENERAL ITEMS

    - Design and procurement for the project needs to be completed to as soon as possible to support current project schedule.

- CLIENT ISSUES/CONCERNS:

    - Location of existing gas line between 7EA and Control Building remains undeterminable after test pitting.

    - Relocation of overhead lines at fuel oil tank area expected to be complete within the next 7 days. Overhead lines will prevent excavation and erection of Raw Water, Demineralized, and Fuel Storage Tanks.

    - Fire line connection and design meeting to be held 6 May 2010. This activity needs to start next week to support current schedule.

    - Septagon, pre-engineered building supplier, to revise foundation drawings to address Sidor’s concerns. This drawing is needed urgently because this building is in the critical path.

- CIVIL:

    - Excavate for cable rack foundations

    - Excavate for duct bank 15 kV Breaker to switchgear

    - Backfill at gas compressor

    - Backfill at Ductbank MH4 to MH 9

    - Conduit excavation 15 kV breaker

    - GT 100 Anchor bolt prep at 7 EA

- CONCRETE FOUNDATIONS:

    - GT 100 Mud Mat Pipe Rack Foundation delayed because of availability of concrete in the area (concrete to be supplied by SIDOR)

    - GT 100 MUD Mat Cable Tray Foundation to GSU delayed because of availability of concrete in the area (concrete to be supplied by SIDOR)

    - Elect. MH 10 Concrete placement walls delayed because of availability of concrete in the area (concrete to be supplied by SIDOR)

    - Blast Wall concrete placement delayed because of availability of concrete in the area (concrete to be supplied by SIDOR)

    - Elect MH 6 Flowable fill delayed because of availability of concrete in the area (concrete to be supplied by SIDOR)

    - Duct Bank Concrete placement GT 200 15 kV Breaker to Load Breaker delayed because of availability of concrete in the area (concrete to be supplied by SIDOR)

- MECHANICAL:

    - GT 100 Confirm turbine piping inventory

    - GT 100 erect puffer manifold system

    - GT 100 Remove engine lifting H Frame

    - GT 100 Ehaust stack seal weld

    - GT 200 Install and torque bolts air filter house

    - GT 200 Install and torque bolts for plenums and roof skids.

    - GT 200 Install air filter walkways

    - GT 300 Exhaust stack weld prep

    - Fabricate pipe for fire line loop

- ELECTRICAL:

    - Install conduit in duct banks

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS:

    - CPS Schedule development on going. First draft being reviewed by the team.

- CRITICAL AREAS OF CONCERN:

    - The lack of availability of cement has caused the delay of numerous concrete pours as shown under Section 4 of this report. Concrete will not be available until Monday, 10 May 2010. 3 day delay

    - Labor demonstrations/strikes prevented the mechanical contractor forces from entering the project site.

    - Design and procurement for the project needs to be completed to as soon as possible to support current project schedule.

    - SAFETY:

      - Develop JSA as needed

      - Inspection of subcontractor power tools.

      - Inspection of motorized equipment prior to usage.

    - OUTSTANDING DRAWINGS:

      - Grounding grid

      - Coordinated underground drawing

      - Switch yard foundations and related duct banks

      - Cable rack foundation drawings

      - Design drawings need to be issued

      - Utility Bldg. Housekeeping pads for electrical equipment.

    - DRAWINGS ISSUED:

      - Foundation Drawing for 15 KV switch

8	PICTURES:

Elect MH 10 Wall Forms and Rebar

GT 100 Excavation for Pipe Rack Foundation

Excavation for Demin Water Tank Engineered Fill

Back Fill Duct Bank MH 9 to MH 4