Table of Contents

1. Executive Summary

EPC

Weekly Report  12 to 18 June 2010Date: 19-June-10Project: Sidor Site B, Puerto Ordaz Venezuela Written By: Cole Franklin ProEnergy EPC Project Mgr

ProEnergy Site Manager

William Lugo

Cole Franklin

1.1 Safety and Regulatory Compliance

1.2 Personnel/Staffing

1.3 Weekly Accomplishments

1.4 Scheduling Conflicts

1.5 Site Manager Commentary and Amplifying Remarks

2. Engineering and Design

2.1 General Arrangement

2.2 Site/Civil/ Structural

2.3 Mechanical

2.4 Electrical

2.5 Instruments & Control

2.6 O&M Manuals

3. Procurement

3.1 Purchase Order Requests

3.2 Equipment & Material Quotations

3.3 Purchase Order

4. Contracts

4.1 EPC Contract

4.2 Construction Subcontracts

4.3 Proposal and Quotes

5. Construction

5.1 Schedule

5.2 Equipment Delivery Status (expediting report)

5.3 Civil

5.3.1 Site Preparation

5.3.2 Centerline Foundation

5.3.3 GSU Foundation

5.3.4 Auxiliary Foundations

5.4.1 Centerline Equipment Installation

5.4.2 Centerline Piping Installation

5.4.3 Auxiliary Piping Installation

5.4.4 Underground Piping Installation

5.4.5 Above Ground Piping Installation

5.4.6 Balance of Plant (BOP) Piping Installation

5.5 Electrical

5.5.1 Duct Bank Installation

5.5.2 Centerline Electrical Installation

5.5.3 Auxiliary Electrical Installation

5.5.4 Balance of Plant (BOP) Installation

5.6 QA/QC

5.6.1 Equipment Testing

5.6.2 Nonconformity Report

5.6.3 Drawing Revisions

5.6.4 CWI Reports

5.6.5 As-built Drawings

6 Start-Up & Commissioning

6.1 Schedule

6.2 Equipment Status

6.3 Punch list

6.4 Equipment Checkout

6.5 Equipment Functional Test

6.6 Equipment Turnover

6.7 Performance Testing

6.8 Emission Testing

7 Mobilization

7.1 Schedule

7.2 Operating Procedure Development

7.3 Operation Staff Training

7.4 Spare Parts/Inventory Status

1. Executive Summary.

This review is for the week from 12 to 18 June 2010.  Safety is good, housekeeping is relaxing, needs attention.  The commercial issues at Site A are continuing to cause problems at Site B.  If we cannot separate the two sites B will continue to have problems caused by issues at site A.   Engineering drawings show a lack of review and attention to details. Material deliveries are still problematic.  Need to develop a means of tracking material from requisition, purchase, shipment, and finally to site, that allows Site to know where the material is in the cycle.

The mud mat for the 7EA unit 100 PEECC was poured on Wednesday.  The backfill installed on the south side of 7EA foundation was not acceptable.  The contractor started the removal of the fill material at Sidor’s request and has since excavated and backfilled the area.   The crane provided by Sidor can be erected on the new fill.   This required a change order to Concorcio.  I prepared a draft CO and sent it to for review, he subsequently released it.

We had problems with the 7EA concrete pour.  We issued a PO for core drilling to test actual installed concrete.  The lateness of the PO did not allow contractor to purchase the drills and start on Friday as planned.  The core drilling started Monday late afternoon, getting a PES sub contractor into Sidor is a problem.  I will discuss with Sidor the possible options to get contractors past Sidor’s gate.  We do not have a contract with Sidor and their procedures keep causing us problems with getting our contractor in.

Contractor quality is good, but contractor lack of craft and equipment is causing slippage of the schedule.  The contractor is willing, but we are nearing the point where Contractor will have no work.  We have forestalled this by moving from 7FA to 7EA stack to PECC, and now starting the oily water separator again.  I am trying to get a PO prepared for a contractor to start duct bank and U/G excavation so we can open up other areas to work on the 7EA.

The 7FA rebar is as far as is possible without embeds and anchor bolts, the Unisorb pre pour package is not at site as of end of this week (on hold).  The anchor bolts for the turbine and auxiliary pkg. are not on site.

Contractor will accept a letter to start work on other areas with PO to follow.  The letter is becoming necessary due to delays in anchor bolts and embeds plates.  Expect to get notice of delays from contractor for missing anchor bolts and embed plates.

1.1 Safety & Regulatory Compliance –

- General Safety will be maintained at all times on site.

- Daily safety audits are now in place, weekly recap to office.

- Contractor installed safety signs on site, marked out traffic lanes to eliminate outside traffic from site and installed a safety bulletin board in their lunch room.  The permanent Bulletin board will be installed when the commercial issues are resolved.

  - Personnel/Staffing –

Cole Franklin (Site Manager)

Keith McMurray (scheduler shared A&B)

Paola Gomez (administrative assist. Local hire)

Patricia Munoz (administrative assist. Local hire)

Daniel Febres (logistics support local hire)

Ysren Gomez (Local hire safety supervisor)

Kyle Rosken (Civil Superintendant shared A &B R&R)

Mark Hawks (Electrical supervisor shared A &B)

Felix Martinez (QA/QC supervisor currently shared A & B)

Paulo Olivio (Material coordinador B)

1.3 Weekly Accomplishments

- The 7EA mud mat for PEECC poured Wed,

- Contractor finished 7EA stack anchor bolts Friday, came up with a plan approved by Wallace to use shorter bolts for stack.

- Contractor has finished 7FA as far as possible awaiting the embeds and anchor bolts

- Contractor has started PEECC base forming, rebar is tied and ready to place into forms.

  - Scheduling Conflicts –

- The duct bank and manholes / hand holes are critical around 7EA.  Still no finalized drawings.  This has a more than 60 day impact on the project.  Received Friday, 18 June, revised SK101 drawings, the originally marked IFC sketches showing pull box locations.  I presented the bid documents, augmented with sketches to Coinserma for a new quote, the quote from the Coinserma group is about 500K Bs less than previous bid.

- The U/G piping comments have not been resolved.

- Plan to issue a sub-contract to start the work of installing duct banks and underground piping, need finalized drawings, but will not wait anymore for them.

- Materials for piping and a large portion of the duct bank conduit are not available at site.

- 7EA PEEC (has a material issue, need embed plates), GSU can not start until crane has de mobilized after setting 7EA on foundation, and 7EA stack need to pour Wednesday), and 7FA need anchor bolts.  I recommend we issue sub-contracts for U/G piping.  This requires engineering and commercial resolution.  The piping materials will be ordered from site if they are not available when we need them.

- The master Bill of Materials for all materials.  We received piping and equipment BOP updated

- Received a P.O. log for all materials ordered to ensure we do not lose more time waiting for material not ordered

1.5– Site Managers Commentary and Amplifying Remarks

The core drilling of the 7
EA slab shows areas of porosity in the cores.  We had a ground radar unit employed to locate the rebar and pipe.  We drilled into one conduit and into several rebar.  This caused to move location of cores and delayed completion.  The ground radar will penetrate 10 M and apparently the top and bottom rebar are not above each other causing false signals.  The cores will be broken Monday or Tuesday.  Contractor entry into Sidor is a major problem must be resolved before we have several contractors working and all out time is devoted to getting contractor personnel into plant.

The progress is not good against the critical path.  I have been in discussions with Coinserma regarding the start of the duct bank and underground.  Coinserma is willing to start as soon as they receive a PO.  I think if the foundation locations are fixed we will start the underground as soon as possible.  I will mark the manhole drawings and determine the elevations based on necessary cover to install hand holes and underground pipe.  This will require a change for the manhole depth.  Sidor did not accept the rebar details in the manholes or hand holes, will red line these and plan to start.

I currently have QA supervisor (shared), scheduler (shared), and electrical supervisor (shared) on site.  I am a little overwhelmed trying to do the PO’s and cash flow and review drawings myself.  EDGI wrote a letter stating we at B are unreasonable in asking for proper drawings, EDGI states there have been more drawings prepared for B than A.  If EDGI checked their own drawings we would not red line them and EDGI would not need to prepare more drawings.  We are seeing some slippage due to the above mentioned items and have no way at present to mitigate the slippage.  I am preparing Change Order drafts for everything I know has been a schedule impact and reviewing the same against the contract.

- Engineering and Design

2.1.1 Received the following drawings this week;

- LCI bldg foundation plans and sections 20-038_1-r1

- Oily water separator details 20-011_2-r1

- Cooling water foundation and pump 20-013_1-r2

- Duct bank sketch SK 101_1-R5 man hole and hand hole locations

- Plant B Septagon building vendor drawings

- 7EA Fuel gas regulator foundation 20-036_1-r0

- Electrical drawings index and interconnect dwgs

- 7FA PEECC foundation plans and sections 20-035_1-r1

2.1.2 Grounding

- The grounding shown on grounding drawings is not in accordance with the discussion with Sidor regarding grounding of equipment.  This will become a major issue.  Need to put it to bed!

2.1.3 Geo tech membrane treated fuel oil tank

- The geo tech fabric needs to be ordered for fuel oil tank received info from engineering, Tracy Gresham, need commercial issue resolution.

  - – Site /Civil /Structural

    - The 7EA PEECC mud mat is complete.

    - 7EA Stack is complete pending pour Wednesday

    - 7FA is pending anchor bolts and embeds.

2.3 – Mechanical –

2.3.1 The 7EA turbine replacement thrust pin plate is being installed. Forecast completion is 6-22-10.

2.3.2 Unisorb fixators not on site for 7FA

2.4 – Electrical –

2.4.1 Duct bank drawings bid package received will award bid, but will red line drawings EDGI indicated we are unreasonable, U/G and duct bank has been priority one since March.

2.5 – Instrumentation - To Be Completed

2.6 – O&M Manuals –

2.6.1 Received 7FA O & M manual, need to transmit to Sidor officially one copy.

3. Procurement

3.1 – Purchase Order Requests

- RFP for anchor bolts 7FA to Sedalia local purchases on hold

- RFP for conduit duct banks north and south 7EA to Sedalia local purchases on hold

- RFP for PEECC embeds to Sedalia local purchases on hold

- RFP for storage container material storages on hold

- RFP for construction power parts (issue CO to Derwick) local purchases on hold

- RFP for construction office distribution panel to local purchases on hold

3.2 – Equipment & Material Quotations –

- In the process Cash flow analysis including all identified PO required

3.3 - Purchase Order

  - Issued PO for core drilling and concrete testing 7EA foundation

4. Contract

4.1 – EPC Contract –

- CO 001 sent of Poor Soils Site B

- CO002 sent for Backfill under crane due to CO001

4.2 – Construction Subcontracts –

  - Negotiation ongoing for actualizing sub-contract for electrical and civil underground, and piping, all works currently slowed for commercial issues and engineering

4.3 – Proposal & Quotes

  - Prepared and issued contract RFP for supplying power to the lay down yard and modifying two sea containers into an office and environmentally controlled storage. Two proposals were received are on hold.

5. Construction

5.1 – Schedule

  - Schedule was issued.  There is significant slippage from original estimates due to soils, labor, material, and engineering issues.  Two week look ahead attached

  - Prepared a Soils Change Order CO 001, now preparing total quantities

  - Prepared a draft Soils Change Order for crane placement for 7EA CO 002

5.2 – Equipment Delivery – in progress

5.2.1 Material issues, early delivery of packing list, and P.O.s are a major problem

5.3 – Mechanical –

5.4 – Electrical –

5.5 QA/QC –

- Ongoing inspections concrete, formworks and anchor bolts.

6 Startup & Commissioning –

7 Startup Mobilization - None

Picture 1: 7EA Stack fdn 18June

Picture 2: 7EA PEECC mud mat 17 June

Picture 3: 7FA awaiting anchor bolts and embeds 18 June