Table of Contents

1. Executive Summary

EPC

Weekly Report  22 -28 May 2010Date: 28-May-10Project: Sidor Site B, Puerto Ordaz Venezuela Written By: Cole Franklin ProEnergy EPC Project Mgr

ProEnergy Site Manager

ProEnergy Construction MgrWilliam Lugo

Cole Franklin

Ted York

1.1 Safety and Regulatory Compliance

1.2 Personnel/Staffing

1.3 Weekly Accomplishments

1.4 Scheduling Conflicts

1.5 Site Manager Commentary and Amplifying Remarks

2. Engineering and Design

2.1 General Arrangement

2.2 Site/Civil/ Structural

2.3 Mechanical

2.4 Electrical

2.5 Instruments & Control

2.6 O&M Manuals

3. Procurement

3.1 Purchase Order Requests

3.2 Equipment & Material Quotations

3.3 Purchase Order

4. Contracts

4.1 EPC Contract

4.2 Construction Subcontracts

4.3 Proposal and Quotes

5. Construction

5.1 Schedule

5.2 Equipment Delivery Status (expediting report)

5.3 Civil

5.3.1 Site Preparation

5.3.2 Centerline Foundation

5.3.3 GSU Foundation

5.3.4 Auxiliary Foundations

5.4.1 Centerline Equipment Installation

5.4.2 Centerline Piping Installation

5.4.3 Auxiliary Piping Installation

5.4.4 Underground Piping Installation

5.4.5 Above Ground Piping Installation

5.4.6 Balance of Plant (BOP) Piping Installation

5.5 Electrical

5.5.1 Duct Bank Installation

5.5.2 Centerline Electrical Installation

5.5.3 Auxiliary Electrical Installation

5.5.4 Balance of Plant (BOP) Installation

5.6 QA/QC

5.6.1 Equipment Testing

5.6.2 Nonconformity Report

5.6.3 Drawing Revisions

5.6.4 CWI Reports

5.6.5 As-built Drawings

6 Start Up & Commissioning

6.1 Schedule

6.2 Equipment Status

6.3 Punch list

6.4 Equipment Checkout

6.5 Equipment Functional Test

6.6 Equipment Turnover

6.7 Performance Testing

6.8 Emission Testing

7 Mobilization

7.1 Schedule

7.2 Operating Procedure Development

7.3 Operation Staff Training

7.4 Spare Parts/Inventory Status

1. Executive Summary.

This review is for the week from 22 May to 28 May 2010.  Safety is good, housekeeping is relatively good.  Due to commercial issues the contractor will not send additional manpower or materials to support the site. They also stated they would not start a second shift at this time.  The lack of completed engineering drawings continues to be a problem. Engineering drawings show a lack of review and attention to details. Material deliveries are still problematic the Bill of Materials for Piping, Electrical, Instruments, and equipment are not available at site.

The new unisorb embeds for 7EA (2- 115 & 1- 116), to replace the ones found damaged in Site A, still have not arrived to the site.  We have proceeded with the original plates and poured the foundation Thursday.

Had problems with the 7EA concrete pour.  The concrete plants were not able to deliver at an acceptable rate, quality of the concrete was not acceptable (high slumps), and found several loads where the batch plant appeared to be having trouble with extra aggregate or sand.  We rejected several trucks and subsequently at about 9 PM had a period where we had no concrete and got a cold joint under the auxiliary module.  The client accepted responsibility for continuing the pour after we recommended stopping, chipping the concrete, installing additional shear bars and making a mechanical joint using a bonding agent. We spoke with Engineering in Tulsa for possible aids to assure the pour was not a complete loss.  They suggested installing additional rebar as shear pins and we continued finishing after 1200 hrs in the night.

Spoke with Sidor Friday morning to schedule a meeting with both batch plant managers and prevent this occurring again on the larger 7FA foundation.  Meeting will be arranged for Monday or Tuesday morning.

Contractor quality is good, but contractor lack of craft and equipment is causing slippage of the schedule.

Contractor has suspended work on everything except the 7EA and rebar for 7FA in order to use the limited resources and materials he has on site. This is unfortunate since we now have additional designs and materials are beginning to arrive to the site.  Contractor requires a change order to work on anything other than the two large foundations.

  - Safety & Regulatory Compliance –

- General Safety will be maintained at all times on site.

- Daily safety audits are now in place, weekly recap to office.

- Contractor installed safety signs on site, marked out traffic lanes to eliminate outside traffic from site and installed a safety bulletin board in their lunch room.

  - Personnel/Staffing –

Cole Franklin (Site Manager)

Ted York (Construction manager) ROF

Melinda Siros (document control)

Keith McMurray (scheduler)

Paola Gomez (administrative assist. Local hire)

Patricia Munoz (administrative assist. Local hire)

Daniel Febres (logistics support local hire)

Ysren Gomez (Local hire safety supervisor)

Kyle Rosken (Civil Superintendant returned to B Wednesday)

Mark Hawks (Electrical supervisor returned to B Wednesday)

Felix Martinez (QA/QC supervisor currently shared A & B)

Ed Dubois (QA/QC tech currently shared A & B) ROF

Paulo Olivio (Material coordinator B) left site for family emergency

Herman Flores (material control Local hire presently Site A)

Jose Angel Gonzales (material control Local hire)

Francisco Gomez (tool room control Local hire presently Site A)

1.3 Weekly Accomplishments

- The 7EA was poured up to the pedestal scheduled for Saturday

- Contractor continues with 7FA rebar only with a small crew.

- We had only a small crew after working until after midnight on the 7EA pour and then rained out afternoon.

1.4 – Scheduling Conflicts –

- Received revised manhole details, handhold details and duct bank plot plan. Comments have been returned to engineering and being reviewed.  The plan to set conduits at 11” below ground and allow field to route will cause problems.  The 90 degree sweeps for 4” are 36” radius

- Received underground piping drawings, review and provided comments to engineering. Design is current around 1.5 to 1.9 meters and below the bottom of adjacent foundations. Excavations in these locations must be performed prior to installation of the foundations.

- PES reviewed the 7FA equipment list and informed engineering that it appears that all of the equipment is not represented on the plot plan.

- PES is concerned that underground utilities are not complete in the current designs. Engineering is reviewing.  This is the critical path and is driving the schedule 2 months at present, the 7FA is presently finishing ahead of the 7EA and the 7FA is at least 2 months more work.

- Plan to issue a sub-contract to start the work of installing duct banks and underground piping.  Materials for piping and a large portion of the duct bank conduit are not available at site.

- This effectively stops all but the 7EA, 7EA PEEC (has a drawings technical issue, requires change order), GSU (has a drawings technical issue, requires change order), and 7EA stack (need to issue a sub-contract to another contractor or change order to Concorcio Megavatio and receive or order the anchor bolts), and 7FA.  Contractor advised in weekly meeting that their management will not work on anything other than 7EA and 7FA without change order, I recommend we issue sub-contracts for this and U/G piping.

- The location plan for the duct bank indicates the foundations available are on top of or very near the duct bank.

- The Bill of Materials and equipment list for all materials and the P.O. log for all materials ordered are now a necessity to ensure we do not lose more time for material delivery delays

  - – Site Managers Commentary and Amplifying Remarks

The progress has been slow for lack of materials, lack of equipment, lack of labor, and lack of engineering.  The client is making life hard in the meetings and we are presently unable to defend ourselves by claiming engineering issues or lack of materials.  The schedule is presently a large issue and we have been hesitant to deliver a schedule that has no history to back it and no change of circumstance to support it.

2 Engineering and Design

2.1 – Received the following drawings this week;

Sketch with coordinates for the duct bank pull box, can start installing duct bank, lack materials.

2.1.1 - The grounding shown on grounding drawings is not in accordance with the discussion with Sidor regarding grounding of equipment.  This will become a major issue.  Need to put it to bed!

2.1.2The water stop for the oily water and waste tanks was resolved.

2.2 – Site /Civil /Structural –

- The 7EA has been poured except pedestal.

- Started installing 7FA vertical rebar mat and some concrete forms.

2.3 – Mechanical –

2.3.1 The 7EA turbine replacement thrust pin plate is being fabricated. Forecast delivery is 5-29-10.

2.4 – Electrical –

2.4.1 Duct bank drawings were issued and engineering is working on comments from the site.

2.5 – Instrumentation - To Be Completed

2.6 – O&M Manuals –

2.6.1 7 EA O & M from another site on site.

3. Procurement

3.1 – Purchase Order Requests

- After discussion at site, due to the receipt of materials not clearly identified by site and by equipment, we will now include the following in all material requisitions:

- The Site “A or B”

- Associated equipment numbers or Balance of Plant equipment or system

- Material specification if applicable

- Who generated the requisition

- Contact information for delivery

- A copy of the P.O. for review after it is produced and before it is released.

- Request for Material certifications.  Site issued a NCR for the anchor bolts in 7EA foundation.  Did not receive material certs or spec with bolts.

- The above will allow QA to assure we have the proper material and segregate it if necessary.

3.2 – Equipment & Material Quotations –

- In the process

3.3 - Purchase Order

3.3.1– Copies of all P.O. to originator after issued and tracking of same by logistics.

3.3.2 – Preparing a list of materials for local purchase for U/G piping and duct banks.

4. Contract

4.1 – EPC Contract –

4.2 – Construction Subcontracts –

  - Negotiation ongoing for actualizing sub-contract for electrical and civil underground, and piping, all works currently slowed for lack of contractor support

4.3 – Proposal & Quotes

  - Prepared and issued contract RFP for supplying power to the lay down yard and modifying two sea containers into an office and environmentally controlled storage. Two proposals were received and are under review.

5. Construction

5.1 – Schedule

- Schedule is being issued.  There is significant slippage from original estimates due to labor, material, and engineering issues.

5.2 – Equipment Delivery – in progress

5.3 – Mechanical –

5.4 – Electrical –

5.5 QA/QC –

- Ongoing inspections on 7EA foundation and concrete pour.

- Discovered lack of documentation for 7EA anchor bolts or proper markings on bolts and nuts. Investigation is in process.

6 Startup & Commissioning –

  - The blank turn over manuals are being prepared for both sites.

7 Startup Mobilization - None

Picture 1: final inspection of 7EA fdn

Picture 2: Installing vertical Rebar for 7FA Foundation

- Picture 3: Concrete placed 7EA