# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 11 June 2010, Friday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  84 F

RANGE: 76 to 89

SITE CONDITIONS: Cool morning, rain mid day, humid, overcast, and hot afternoon

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Project Mgr (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Mark Hanks - Electrical Supt (A&B)

Kyle Roskam - Civil Supt (R&R)

Felix Martinez-QA/QC (A&B)

MATERIAL SUPPORT:

Jose Angel Gonzales – Materials (Local)

Paul Oliva – Materials

ADMIN SUPPORT:

Daniel Febres – Logistics (Local)

Paola Gómez – Admin (Local)

Patricia Munos – Admin (Local)

Skeila Garcia – Translator & Doc Control (Local)

SUBCONTRACTOR PERSONNEL:

General Superintendant		1

Safety					1

Foremen				5

Electricians				0

Operators				3                        Surveyor				1

Carpenters				7    Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				4

Truck Drivers				2

Concrete Finishers			0

Oilers					2

Plumbers				0                        Iron Workers				10

Helpers				8

Welders				3

Total:					44

- GENERAL ITEMS:

  - GSU for Site A damaged in transit.  Received no update this issue.

  - Need plot plan showing reduced BERM for Diesel tank, need to determine if moving the Over Head 13.8 line is necessary.

  - 7EA stack the schedule will be impacted if no anchor bolts by 15 June, due to commercial issues, and not being able to place purchase orders, have sent a consolidated PO log for all anchor bolts and embeds on the critical path for next three weeks.

  - I have had a 4 day slippage on the schedule on the Unit 200 (7FA) for lack of anchor bolts as of today.  Contractor will probably notify us we are delaying his work next week due to lack of foundation materials.

  - Need to order Geo Tech Membrane if necessary for Treated fuel oil tank.

  - Proposal for modifying sea containers for lay down area office, temperature controlled storage and running power to area offer is on hold pending resolution of commercial issues.

  - RFP for trash containers and disposal of trash is prepared pending new quotes, and commercial issue resolution.

  - Site continues a material takeoff of drawings available at site, will conclude the piping when possible.  Need to order piping materials, asked EDGI if the updated piping BOM is available, also asked if the road crossings will be shown on drawings.  Sidor has indicated any place a crane can pass is a road crossing.  Need to consider this when ordering materials including conduit.

  - The electrical contractor has asked for a meeting to discuss the drawings that are supposed to be IFC today.  I asked them to put it off till Monday morning.

  - Batch plants advised there will be no concrete due to lack of cement 20 to 27 June.  This was in the window for pouring the 7FA foundation; the date is now in question.

  - Sidor crane finally started mobilization.  Will take a week to finalize.  The crane requires we issue a PO for excavation and back fill with engineered fill.  The soils will not support the crane without this fill.

- CLIENT ISSUES/CONCERN:

  - Progress on Foundation 7FA need first order of anchor bolts, the order was agreed to place, but the manufacturer has not delivered a copy of the mill certs Bill Lugo spoke to Brett and it was agreed to release PO for 7EA slab and small order for anchor bolts for 7EA.

  - Underground piping and duct bank drawings dwgs delayed to 11 June, will discard the sketches and provide IFC drawings.  This is a big issue.  The electrical drawings were received today “issued for BID” cover says not for construction.  This is another 1 week delay to total project.  The package is hard to read, incomplete, and not suitable for delivering to a contractor.  I will spend the time and review them Saturday and Sunday and try to deliver a list of the necessary actions to prepare this for issue.  They need to be IFC not for bid, we can start as soon as the drawings are available and we can issue a PO to start the contractor.

  - Request for purchase for trash bins for site lay down area and construction site released RFP for delivery dates. Sidor was asked to provide this, but never delivered.

  - Sidor to delivered fire water flow rates for Plant B, I forwarded the information to Shane D.

  - Commercial issues and causing a serious impact on purchasing materials to continue work.

- CIVIL:

  - Concrete issues; lack of cement 20 to 27 June, lack of proper cement type III only will be available.

  - Lack of anchor bolts for 7EA stack foundation

  - Lack of anchor bolts for 7FA foundation

  - Lack Embeds for PEECC

  - Lack Piping for U/G

  - Lack of materials for Oily water separator

  - Lack of resolution for Treated Fuel Oil Tank

- CONCRETE FOUNDATIONS:

4.1 Work today on the 7FA with small crew of manpower.  The work is progressing very slowly due to the lack of manpower and materials.  The contractor will be ready to install anchor bolts and Unisorb starting Thursday delayed for bolts.  The Post pour and pre pour Unisorb is being sent via air freight according to Kyle.

4.3 Contractor agreed to continue with all 7EA equipment including GSU, PEECC, and Stack.

4.4 Issued RFP for 7EA anchor bolts, delivery 5 days 71,000 Bs. On hold

4.5 Issued RFP for PEECC embeds. On hold

4.6 Received quotation for core drilling.  Bs44710. Or about $9000. USD released this PO, but the contractor cannot mobilize this week due to lateness of PO being issued (5:00 PM yesterday) he ordered the core drill bit after receipt.

4.7 Need to write a letter to Concorcio advising them to install fill to set up the crane.  The fill is about 900 M3 at about BS90. (Bolivars per meter cubed) or about 18,000Bs

- MECHANICAL:

5.1 7EA generator replacement jib base plate is finished in Sedalia. Tom Koontz         has ship by air freight to site. Arrived Caracas last night, forwarded to Puerto Ordaz today.

5.2 Requested ISI to provide insurance certifications.  They expect to have insurance certificate and all Sidor documents by Tuesday.

5.3 Ready to install anchor bolts for 7EA stack foundation today.

- PIPING:

6.1 Review ongoing of material takeoff for bulk order of piping.

6.1 Need BOM and marked sketch showing road crossing for duct bank and U/G piping, otherwise Sidor has indicated we should treat any area where crane can pass as a road crossing.

- ELECTRICAL:

7.1 Will add a lighting breaker panel for office trailers, very concerned for the “piggybacking” of wires into the breaker we installed. On hold awaiting resolution of commercial issues

7.2 Concorcio gave us a list of materials for the site construction power transformer installation. Sidor (Daniel) called and says PES should provide this material. Prepared a RFP for material will hold awaiting resolution of commercial issues, spoke to Sidor today for this and will prepare a CO to Derwick.

7.3 The embeds for GSU are different than site “A”, will get the foundation changed to match “A” to create less problems because “B” is different.  We will red line and continue same as “A”.

7.4 The sub contractor Coinserma came to site for meetings regarding the duct bank work.  The review of the quote is about 30% high in my estimate, but about 30% of the cost for comparable work by Concorcio.  The commercial issue as well as the materials makes this impossible to issue, have a meeting Monday to attempt to drive down the price after review of the bid package received today.   Lack of finalized drawings has delayed the project an additional week at this point, not including commercial issues.

7.5 The underground piping and duct bank is now critical path and is driving the schedule, can afford no more delays.

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS: 9.1 General Schedule issues The schedule is predicated by the following: - Commercial issues are resolved to local purchase materials - Contractor increases manpower to work in all areas - Contractor works two shifts - The Underground and duct bank is started next week and does not slip more - Sedalia material delivers are forthcoming to meet demand 9.2 Milestone Payment Estimated Delivery - Completed Milestone Payments (50%) Complete - Gas Turbines on Foundation (10%) July 19, 2010 this will probably slip one week unless we can come up with an incentive to contractor to accelerate the schedule and can receive the materials for the foundation - Civil Foundations Complete (25%) Sep 15, 2010 (*) - Electrical/Mechanical Complete (10%) Dec 3, 2010 (*) - Start- up Complete and Ready to Export Power (5%) Dec 11, 2010 (*) Note (*): These dates are estimated based on current uncertain conditions (lack of payment, cash issues, material/equipment deliveries on hold, contractors working at very slow pace, etc).. They will be revised as soon as the schedule review is complete and a clearer path forward is known. 9.3 Payment milestones - Unit 100 – 7EA Nov 29, 2010 (*) - Unit 200 – 7FA Dec 11, 2010 (*)

- CRITICAL AREAS OF CONCERN:

  - Sidor provided crane started to mobilize, I understand it takes a week to mobilize.  Mobilization now on hold for lack of excavation and installation of compacted fill material.

  - Changes in designs are impacting project progress/completion.

  - Shortage of cement is affecting the scheduling of foundations.

  - Duct Bank drawings now forecast for Monday 11Jun10.  Not issued for construction

  - Material deliveries and the trickle down caused by commercial issues seriously retard our ability to execute schedule

  - SAFETY:

    - Concorcio Megavatio reported job site information board was assembled and ready to bring to site for installation.   Pending resolution of commercial issues.

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| GSU 7EA | 15May10 | 25May10 | Received a bid package today 11 June not IFC |
| Balance of FDN drawings | 25May10 | 3Jun10 | slipped |
| Treated Fuel Tank updated drawings | 29May10 | 1Jun10 | slipped |
| U/G piping | 5May10 | 28May10 | slipped |
| GSU 7FA | 21May10 | 2 Jun10 | slipped |
| Duct Bank | Had sketch to use for bid review | 11 June 10 | Received a bid package today 11 June not IFC |
| Design essentially complete | 31 May | No forecast date |  |

    - A spread sheet of all the pending drawing issues noted here is being consolidated; these issues will be captured for both sites.

    - After review of the duct bank drawings EDG needs to perform an evaluation the dimensions shown they do not reconcile with depths mentioned in discussions.  IF all is equal to drawings there is no room for piping to cross over duct banks.  The handhold elevation will not cover 4” 36” radius 90 degree turns in conduit.

  - ISSUED DRAWINGS:

Electrical interconnect drawings

11. PICTURES: Same photos as yesterday shows same issues

Photo 1: 7FA Pedestal rebar ongoing

Photo 2: 7EA backfill for crane 7EA