# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 15 June 2010, Tuesday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  87 F

RANGE: 77 to 91

SITE CONDITIONS: Overcast all day

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Project Mgr (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local) off

Keith McMurray - Scheduler (A&B)

Mark Hanks - Electrical Supt (A&B)

Kyle Roskam - Civil Supt (R&R)

Felix Martinez-QA/QC (A&B)

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Paul Oliva – Materials

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local)

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila Garcia – Translator & Doc Control (Local)

SUBCONTRACTOR PERSONNEL:

General Superintendant		1

Safety					1

Foremen				5

Electricians				0

Operators				3                        Surveyor				1

Carpenters				7    Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				4

Truck Drivers				2

Concrete Finishers			0

Oilers					2

Plumbers				0                        Iron Workers				10

Helpers				8

Welders				3

Total:					44

- GENERAL ITEMS:

  - Contractor advised they are now working a 48 hr work week, effective today.  They will work 5 days per week only until further notice.

  - Changed meeting times with contractor to Tuesday and Thursday at 2:00 
PM

  - Little work on 7FA foundation, the anchor bolts and Unisorb pre pour package are not on site.  Lack of anchor bolts is a day per day delay to schedule.

  - 7EA stack the schedule will be impacted.  The pour for the 7EA stack was canceled for Thursday.  Sidor wanted confirmation we would have bolts on 15 June, had to advise them until commercial issues resolved no bolts will be shipped.  We are not able to place purchase orders, have sent a consolidated PO log for all anchor bolts and embeds on the critical path for next three weeks.

  - Will try to work on oily water separator next week to keep contractor busy.  Requested concrete today for the mud mat on the 16 June.  This is cancelled the coordinates on drawing 20-001 sht 1 rev 13 are different than the excavation which is completed.

  - Received underground and duct bank dwgs issued for bid, need IFC to continue foundations around 7EA.  I asked the contractor to propose an adjusted fixed fee contract with unit prices.

  - Need plot plan showing reduced BERM for Diesel tank, need to determine if moving the Over Head 13.8 line is necessary.  This is also essential in starting the storm drains.

  - Need to order Geo Tech Membrane if necessary for Treated fuel oil tank.

  - Proposal for modifying sea containers for lay down area office, temperature controlled storage and running power to area offer is on hold pending resolution of commercial issues.

  - RFP for trash containers and disposal of trash is prepared pending new quotes, and commercial issue resolution.

  - Site continues a material takeoff of drawings available at site, will conclude the piping when possible.

  - Batch plants advised there will be no concrete due to lack of cement 20 to 27 June.  There is no way to pour 7FA this week as of right now.

  - Sidor crane finally started mobilization.  Will take a week to finalize.  The crane requires we issue a PO for excavation and back fill with engineered fill.  The soils will not support the crane without this fill.  Prepared a CO to Derwick for this, Bill will submit to Derwick.

  - GSU for Site A damaged in transit.  Received no update this issue.

- CLIENT ISSUES/CONCERN:

  - Client is asking to move one person into our office at site.

  - Client asked about material availability to continue on 7FA foundation and 7EA stack, I assured them we have permission for the PO for core drilling, and partial anchor bolts.  The anchor bolt manufacturer delivered a copy of the mill certs wrong material.

  - Client (Daniel) was concerned for lack of engineering.  I was asked if EDGI has sufficient engineers.  Daniel noted all mechanical dwgs are all by LES and that there does not seem to be any follow up to their questions and the drawings showing the changes requested are slow or not forthcoming.  He is concerned EDG may be overloaded.

  - Request for purchase for trash bins for site lay down area and construction site released RFP for delivery dates. Sidor was asked to provide this, but never delivered.

- CIVIL:

  - Concrete issues; lack of cement 20 to 27 June, lack of proper cement type III only will be available.

  - Lack of anchor bolts for 7EA stack foundation delay two day

  - Lack of anchor bolts for 7FA foundation continued delay,  Contractor advises he will be without work after Thurday

  - Lack Embeds for PEECC need by 19 June

  - Lack Piping for U/G

  - Lack of materials for Oily water separator including water stop

  - Lack of resolution for Treated Fuel Oil Tank

  - Soils where crane must be located are not suitable for setting crane to install turbine and generator on 7EA.  Prepared CO number 002

- CONCRETE FOUNDATIONS:

4.1 Work today on the 7FA with small crew of manpower.  The work is progressing very slowly due to the lack of manpower and materials.  The contractor needs to install anchor bolts and Unisorb immediately.  The Unisorb anchor bolts are on hold to ship.

4.3 Contractor agreed to continue with all 7EA equipment including GSU, PEECC, and Stack.

4.4 Issued RFP for 7EA anchor bolts, delivery 5 days 71,000 Bs. On hold

4.5 Issued RFP for PEECC embeds. On hold

4.6 Contractor drilled cores to test for the 7EA.  Continues

4.7   Need to write a letter to Concorcio advising them to install fill to set up the crane.  Met with crane supervisor this morning, he advises that an area of 30 X 30 is not necessary.  The graphic he sent is not drawn to scale.  He requires an area 19M X 19M X 1M deep plus an area each end of the crane pad for access by truck of 5M X 10M X 1M deep.  The excavation is 620M3 at 50 per meter and fill is about 500 M3 at about BS90. Excavation of water saturated fill and unstable fill is included USD $12500.  Wrote change order based on contractor quotation and extended overhead asking for 14 day delay.

- MECHANICAL:

5.1 7EA generator replacement jib base plate arrived at site at about 8AM. Jason Byrd moved it to the lay down yard to start installation.

- PIPING:

6.1 Review ongoing of material takeoff for bulk order of piping.  Will prepare a PO for the material delta.

6.1 Received BOM U/G piping today.  Sidor has indicated we should treat any area where crane can cross as a road crossing.

- ELECTRICAL:

7.1 Will add a lighting breaker panel for office trailers, very concerned for the “piggybacking” of wires into the breaker we installed this is a safety issue.  We were without power most of the morning, but proved to be another issue. On hold awaiting resolution of commercial issues

7.2 Concorcio gave us a list of materials for the site construction power transformer installation. Sidor (Daniel) called and says PES should provide this material. Prepared a RFP for material will hold awaiting resolution of commercial issues, spoke to Sidor today for this and will prepare a CO to Derwick.

7.3 The embed plates for the GSU are different than site “A”, we will order the embeds, Site “A” will also change and install the new embeds after the fact.

7.4 The sub contractor Coinserma is preparing a new bid against new drawings.  This will be very hard to quantify.  There are no dimensions, and quantity take off is impossible.  There is no legend so it will require a large amount of PES time to supervise this work.

7.5 The underground piping and duct bank is now critical path and is driving the schedule, can afford no more delays.

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS: 9.1 General Schedule issues The schedule is predicated by the following: - Commercial issues are resolved to local purchase materials - Contractor increases manpower to work in all areas - Contractor works two shifts - The Underground and duct bank is started next week and does not slip more - Sedalia material delivers are forthcoming to meet demand 9.2 Milestone Payment Estimated Delivery - Completed Milestone Payments (50%) Complete - Gas Turbines on Foundation (10%) July 19, 2010 this has slipped, we must come up with an incentive to contractor to accelerate the schedule and we must receive the materials for the foundations - Civil Foundations Complete (25%) Sep 15, 2010 (*) see above - Electrical/Mechanical Complete (10%) Dec 3, 2010 (*) see above - Start- up Complete and Ready to Export Power (5%) Dec 11, 2010 (*) Note (*): These dates are estimated based on current uncertain conditions (lack of payment, cash issues, material/equipment deliveries on hold, contractors working at very slow pace, etc).. They will be revised as soon as the schedule review is complete and a clearer path forward is known. 9.3 Payment milestones - Unit 100 – 7EA Nov 29, 2010 (*) - Unit 200 – 7FA Dec 11, 2010 (*)

- CRITICAL AREAS OF CONCERN:

  - Sidor provided crane started to mobilize, add a week to set up crane on site after backfill.  Crane setup now on hold for lack of excavation and installation of compacted fill material.

  - Lack of materials (anchor bolts 7EA stack, embed plates 
PEECC 7EA, and water stop for Oily water seperator

  - Changes in designs are impacting project progress/completion.

  - Need finalized design or if that cannot be completed, need to include all equipment on GA and freeze the design with Sidor approval.

  - Shortage of cement is affecting the scheduling of foundations.

  - Duct Bank drawings no new forecast for issued for construction drawings

  - Material deliveries and the trickle down caused by commercial issues seriously retard our ability to execute schedule

  - SAFETY:

    - Concorcio Megavatio reported job site information board was assembled and ready to bring to site for installation.   Pending resolution of commercial issues.

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| GSU 7EA | 15May10 | 25May10 | Received a bid 11 June not IFC |
| Balance of FDN drawings | 25May10 | 3Jun10 | slipped |
| Treated Fuel Tank updated drawings | 29May10 | 1Jun10 | slipped |
| U/G piping | 5May10 | 28May10 | slipped |
| GSU 7FA | 21May10 | 2 Jun10 | slipped |
| Duct Bank | Had sketch to use for bid review | 11 June 10 | Received a bid 11 June not IFC |
| Design essentially complete | 31 May | No forecast date | No forecast date |

    - A spread sheet of all the pending drawing issues noted here is being consolidated; these issues will be captured for both sites.

10.8.2 After review of the duct bank drawings EDG needs to perform an evaluation the dimensions shown they do not reconcile with depths mentioned in discussions.  IF all is equal to drawings there is no room for piping to cross over duct banks.  The handhold elevation will not cover 4” 36” radius 90 degree turns in conduit.

  - ISSUED DRAWINGS:

BOM Piping

BOM Equipment

11. PICTURES: No new photos camera disappeared