# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 19 June 2010, Saturday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  91 F

RANGE: 79 to 92

SITE CONDITIONS: Partial sun to overcast

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Project Mgr (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)off

Keith McMurray - Scheduler (A&B)

Mark Hanks - Electrical Supt (A&B)

Kyle Roskam - Civil Supt (R&R)

Felix Martinez-QA/QC (A&B)

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local) off

Paul Olivo – Materials off

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local) off

Paola Gómez – Administración (Local) off

Patricia Muños – Administración (Local) off

Skeila Garcia – Translator & Doc Control (Local)off

SUBCONTRACTOR PERSONNEL:

General Superintendant		0

Safety					0

Foremen				0

Electricians				0

Operators				0                        Surveyor				0

Carpenters				0    Surveyor Helper			0

Oiler Helper				0

Crane Operator			0                           Laborers				0

Truck Drivers				0

Concrete Finishers			0

Oilers					0

Plumbers				0                        Iron Workers				0

Helpers				0

Welders				0

Total:					0

- GENERAL ITEMS:

  - No contractor work today

  - Sidor crane back fill with engineered fill was finished yesterday. Sidor requested  to contractor to start.  It will take a week after the backfill to erect the crane.  CO to Derwick pending for soils.

  - Preparing cash flow analysis for next 8 weeks

  - Preparing PO for pipe, electrical contractor underground

  - Preparing PO for cable tray supports and pipe rack

- CLIENT ISSUES/CONCERN:

  - Client is asking to move one person into our office at site.

  - Client advised they do not accept the response from EDGI regarding location of Treated Fuel tank.

  - Client has sent a flurry of e-mail to EDGI regarding engineering issues.

- CIVIL:

  - Concrete issues; lack of cement 20 to 27 June, lack of proper cement type III only will be available.

  - 7EA stack foundation pour delayed until next Wednesday

  - Lack of anchor bolts for 7FA foundation continued delay; Contractor will be working on PEECC foundation base and oily water separator.

  - Lack Embeds for PEECC need by 21 June, the mud mat for PEECC is poured.

  - Lack Piping for U/G

  - Lack of materials for Oily water separator including water stop.  Will follow Plant A lead this issue

  - Lack of resolution for Treated Fuel Oil Tank location.  Received information from Tracy for Geotech membrane.

  - Soils where crane must be located are not suitable for setting crane to install turbine and generator on 7EA.  Prepared CO number 002.

- CONCRETE FOUNDATIONS:

  - Issued RFP for 7EA anchor bolts, On hold

  - Issued RFP for PEECC embeds. On hold

  - Contractor drilled cores to test for the 7EA.  Prepare for testing next week.

  - No response from Pressure Grout Company, have not located another to check pricing.

  - Wrote change order based on contractor quotation for crane backfill and extended overhead asking for 14 day delay.  This might not be enough based on commercial issues preventing execution.

- MECHANICAL:

5.1 7EA generator replacement jib base plate arrived at site at about 8AM. Jason Byrd advised it is complete.

- PIPING:

6.1 Review ongoing of material takeoff for bulk order of piping.  Preparing a PO for the material.

6.1 Received BOM U/G piping from EDGI.  Sidor has indicated we should treat any area where crane can cross as a road crossing.

- ELECTRICAL:

7.1 Will add a lighting breaker panel for office trailers, very concerned for the “piggybacking” of wires into the breaker we installed this is a safety issue.  We were without power most of the morning, but proved to be another issue. On hold awaiting resolution of commercial issues

7.2 Concorcio gave us a list of materials for the site construction power transformer installation. Sidor (Daniel) called and says PES should provide this material. Prepared a RFP for material will hold awaiting resolution of commercial issues, spoke to Sidor today for this and will prepare a CO to Derwick.

7.3 The embed plates for the GSU are different than site “A”, RFP prepared and quotation available to  order the embeds, Site “A” will also change and install the new embeds after the fact.  On hold

7.4 The sub contractor Coinserma prepared a new bid.  I meet with them today to finalize this.  This execution will require a large amount of PES time to supervise this work.

7.5 The underground piping and duct bank is now critical path and is driving the schedule, can afford no more delays.

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Commercial issues are resolved to local purchase materials

- Contractor increases manpower to work in all areas

- Contractor works two shifts

- The Underground and duct bank is started week of 7 June and does not slip more

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (50%)

Complete

- Gas Turbines on Foundation (10%)

July 19, 2010 this has slipped, we must come up with an incentive to contractor to accelerate the schedule and we must receive the materials for the foundations

- Civil Foundations Complete (25%)

Sep 15, 2010 (*) see above

- Electrical/Mechanical Complete (10%)

Dec 3, 2010 (*) see above

- Start- up Complete and Ready to Export Power (5%)

Dec 11, 2010 (*)

* Note (*): These dates are estimated based on current uncertain conditions (lack of payment, cash issues, material/equipment deliveries on hold, contractors working at very slow pace, etc).. They will be revised as soon as the schedule review is complete and a clearer path forward is known.

9.3 Payment milestones

- Unit 100 – 7EA

Nov 29, 2010 (*)

- Unit 200 – 7FA

Dec 11, 2010 (*)

- CRITICAL AREAS OF CONCERN:

  - The 7EA foundation concrete breaks are below acceptable; the core drilling has indicated an area in the suspect zone of porous concrete.  We are exploring a pressure grout company to grout this zone so we can hope to continue with erection of Turbine and Generator.

  - Sidor provided crane started to mobilize, add a week to set up crane on site after backfill.  Backfill completed Friday.

  - Lack of materials (anchor bolts 7EA stack, embed plates 
PEECC 7EA, and water stop for Oily water separator

  - Changes in designs are impacting project progress/completion.

  - Need finalized design or if that cannot be completed, need to include all equipment on GA and freeze the design with Sidor approval.

  - Shortage of cement is affecting the scheduling of foundations.

  - Duct Bank drawings new forecast 28 June, for issued for construction drawings

  - Material deliveries and the trickle down caused by commercial issues seriously retard our ability to execute schedule

  - Unable to connect to internet today.

  - SAFETY:

    - Concorcio Megavatio reported job site information board was assembled and ready to bring to site for installation.   Pending resolution of commercial issues.

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| Balance of FDN drawings | 25May10 | 3Jun10 | No idea |
| Treated Fuel Tank updated drawings | 29May10 | 1Jun10 | No idea |
| Duct Bank | 17May | 28 June 10 |  |
| Design essentially complete | 31 May | No forecast date | No forecast date |

10.11.2 After review of the duct bank drawings EDG needs to perform an evaluation the dimensions shown they do not reconcile with depths mentioned in discussions.  IF all is equal to drawings there is no room for piping to cross over duct banks.  The handhold elevation will not cover 4” 36” radius 90 degree turns in conduit.

  - ISSUED DRAWINGS:

11. PICTURES:

Photo 1: 7EA stack foundation

Photo 3: 7EA PEECC mud mat