# CVG SIDOR POWER PROJECT SITE “B”

# DATE: 21 June 2010, Monday # PROJECT #: 410-3203 # SITE MANAGER: Cole Franklin

TEMPERATURE:  85 F

RANGE: 79 to 87

SITE CONDITIONS: heavy rain morning, showers after

PERSONNEL ON SITE:

CONSTRUCTION SUPPORT:

William Lugo - Project Mgr (A&B)

Cole Franklin - Site Manager

Ysrin Gomez – Local Safety (Local)

Keith McMurray - Scheduler (A&B)

Mark Hanks - Electrical Supt (A&B)

Kyle Roskam - Civil Supt (R&R)

Felix Martinez-QA/QC (A&B)

MATERIAL SUPPORT:

José Ángel Gonzales – Material (Local)

Paul Olivo – Materials

ADMIN SUPPORT:

Daniel Febres – Logísticas (Local) parcial

Paola Gómez – Administración (Local)

Patricia Muños – Administración (Local)

Skeila Garcia – Translator & Doc Control (Local)

SUBCONTRACTOR PERSONNEL:

General Superintendant		1

Safety					1

Foremen				3

Electricians				0

Operators				0                        Surveyor				1

Carpenters				7    Surveyor Helper			2

Oiler Helper				0

Crane Operator			0                           Laborers				4

Truck Drivers				0

Concrete Finishers			0

Oilers					0

Plumbers				0                        Iron Workers				10

Helpers				4

Welders				2

Total:					35

- GENERAL ITEMS:

  - The core drilling of the 7EA foundation showed porosity in the concrete from about 8” to 12” into the foundation.  The cores will be tested tomorrow.  One core penetrated a conduit, even though we had a metal detector locate the installed bar and conduits before drilling.  We will repair after the cores are tested.

  - Contacted a pressure grouting company to come to site to prepare a quote and advise what is necessary to start this work as soon as possible.  No response today, have asked to locate another company.

  - Little work on 7FA foundation, the anchor bolts and Unisorb pre pour package are not on site.  Lack of anchor bolts is a day per day delay to schedule.

  - We will pour 7EA stack 100+ M3 on Wed. morning.

  - Will pour the base for PEECC 12M3 Wed. morning.

  - The mud mat for oily water separator may pour next week the completed excavation on site will be used.  Have included the 4 M3 in Wednesday pour.

  - I asked the contractor to propose an adjusted fixed fee contract with unit prices for underground and duct bank.  Contractors quote is approximately 500k Bolivars less than original.  We are preparing the PO for signature and hopefully start this week.  We will modify the IFC sketches previously delivered by EDGI.  EDGI promised IFC drawings for 7 and 11 June, we have been unable to get EDGI to resolve the elevation bust in top of duct banks.

  - Need plot plan showing reduced BERM for Diesel tank, need to determine if moving the Over Head 13.8 line is necessary.  This is also essential in starting the storm drains.

  - Need to order Geo Tech Membrane if necessary for Treated fuel oil tank.

  - Proposal for modifying sea containers for lay down area office, temperature controlled storage and running power to area offer is on hold pending resolution of commercial issues.

  - RFP for trash containers and disposal of trash is prepared pending new quotes, and commercial issue resolution.

  - Site continues a material takeoff of drawings available at site, will conclude the piping when possible.

  - Sidor crane back fill with engineered fill was finished Friday. Sidor requested to contractor to start.  It will take a week after the backfill to erect the crane.  CO to Derwick pending for soils.

  - GSU for Site A damaged in transit.  Have heard there is no damage, as soon as the crane sets the 7EA turbine and generator we will start GSU foundation, need GSU embeds PO on hold

- CLIENT ISSUES/CONCERN:

  - Client is asking to move one person into our office at site.

  - Client advised they do not accept the response from EDGI regarding location of Treated Fuel tank.

  - Client has sent a flurry of e-mail to EDGI regarding engineering issues.

  - Request for purchase for trash bins for site lay down area and construction site released RFP for delivery dates. Sidor was asked to provide this, but never delivered.

- CIVIL:

  - Concrete issues; lack of cement 20 to 27 June, lack of proper cement type III only will be available.

  - 7EA stack foundation pour delayed until next Wednesday

  - Lack of anchor bolts for 7FA foundation continued delay; Contractor will be working on PEECC foundation base and oily water separator.

  - Lack Embeds for PEECC need by 21 June, the mud mat for PEECC is poured.  Expect to pour base for PEECC Wed.

  - Lack Piping for U/G.  Material on hold in Houston to ship PO INTL4475 Genoyer

  - Lack of materials for Oily water separator including water stop.  Will follow Plant A lead this issue

  - Lack of resolution for Treated Fuel Oil Tank location.

  - Preparing PO for local purchase for Geotech membrane.

  - Soils where crane must be located are not suitable for setting crane to install turbine and generator on 7EA.  Prepared CO number 002.

- CONCRETE FOUNDATIONS:

  - Work today on the 7FA was halted by contractor.

  - Issued RFP for 7EA stack anchor bolts, totally cancelled

  - Issued RFP for 7FA Unisorb anchor bolts, local cancelled

  - Issued RFP for PEECC embeds. On hold

  - Contractor drilled cores to test for the 7EA.  Will test cores tomorrow, have asked Sidor to witness test.  No time forecast as of today at 4PM for test tomorrow.

  - Wrote change order based on contractor quotation for crane backfill and extended overhead asking for 14 day delay.  This might not be enough based on commercial issues preventing execution.

- MECHANICAL:

5.1 7EA generator replacement jib base plate arrived at site at about 8AM. Jason Byrd has completed Welding Jib plate.

- PIPING:

6.1 Review ongoing of material takeoff for bulk order of piping.  Received the PO from Pam Arnold for Genoyer

6.1 Received BOM U/G piping from EDGI.  Sidor has indicated we should treat any area where crane can cross as a road crossing.

- ELECTRICAL:

7.1 Will add a lighting breaker panel for office trailers, very concerned for the “piggybacking” of wires into the breaker we installed this is a safety issue.  We were without power most of the morning, but proved to be another issue. On hold awaiting resolution of commercial issues, with all the rain have asked this be turned on.

7.2 Concorcio gave us a list of materials for the site construction power transformer installation. Sidor (Daniel) called and says PES should provide this material. Prepared a RFP for material will hold awaiting resolution of commercial issues, spoke to Sidor today for this and will prepare a CO to Derwick.

7.3 The embed plates for the GSU are different than site “A”, RFP prepared and quotation available to order the embeds, Site “A” will also change and install the new embeds after the fact.  On hold

7.4 The sub contractor Coinserma prepared a new bid.  I met with them today and they wish to mobilize at their risk.  The execution of this scope will require a large amount of PES time to supervise this work.  Today received and e-mail from EDGI, we will cancel the manholes drawings and use Sidor’s design.

7.5 The underground piping and duct bank is now critical path and is driving the schedule, can afford no more delays.

- INSTRUMENTATION AND CONTROLS:

- SCHEDULED ITEMS:

9.1 General Schedule issues

The schedule is predicated by the following:

- Commercial issues are resolved to local purchase materials

- Contractor increases manpower to work in all areas

- Contractor works two shifts

- The Underground and duct bank is started week of 7 June and does not slip more

- Sedalia material delivers are forthcoming to meet demand

9.2 Milestone Payment Estimated Delivery

- Completed Milestone Payments (50%)

Complete

- Gas Turbines on Foundation (10%)

July 19, 2010 this has slipped, we must come up with an incentive to contractor to accelerate the schedule and we must receive the materials for the foundations

- Civil Foundations Complete (25%)

Sep 15, 2010 (*) see above

- Electrical/Mechanical Complete (10%)

Dec 3, 2010 (*) see above

- Start- up Complete and Ready to Export Power (5%)

Dec 11, 2010 (*)

* Note (*): These dates are estimated based on current uncertain conditions (lack of payment, cash issues, material/equipment deliveries on hold, contractors working at very slow pace, etc).. They will be revised as soon as the schedule review is complete and a clearer path forward is known.

9.3 Payment milestones

- Unit 100 – 7EA

Nov 29, 2010 (*)

- Unit 200 – 7FA

Dec 11, 2010 (*)

- CRITICAL AREAS OF CONCERN:

  - The 7EA foundation concrete breaks are below acceptable; the core drilling has indicated an area in the suspect zone of porous concrete.  We are exploring a pressure grout company to grout this zone so we can hope to continue with erection of Turbine and Generator.

  - Sidor provided crane started to mobilize, add a week to set up crane on site after backfill.  Crane setup now on hold for lack of excavation and installation of compacted fill material which is expected to finish Monday

  - Lack of materials (anchor bolts 7EA stack, embed plates 
PEECC 7EA, and water stop for Oily water separator

  - Changes in designs are impacting project progress/completion.

  - Need finalized design or if that cannot be completed, need to include all equipment on GA and freeze the design with Sidor approval.

  - Shortage of cement is affecting the scheduling of foundations.

  - Duct Bank drawings new forecast 28 June, for issued for construction drawings

  - Material deliveries and the trickle down caused by commercial issues seriously retard our ability to execute schedule

  - Unable to connect to internet today.

  - SAFETY:

    - Concorcio Megavatio reported job site information board was assembled and ready to bring to site for installation.   Pending resolution of commercial issues.

  - OUTSTANDING DRAWINGS:

| Drawings Issue | Forecast date | New F/C date | Closed |
| --- | --- | --- | --- |
| GSU 7EA | 15May10 | 25May10 | Will pour when crane moves after setting unit 100 turbine generator |
| Balance of FDN drawings | 25May10 | 3Jun10 | No idea |
| Treated Fuel Tank updated drawings | 29May10 | 1Jun10 | No idea |
| U/G piping | 5May10 | 28May10 | No idea |
| GSU 7FA | 21May10 | 2 Jun10 | Not critical |
| Duct Bank | 17May | 28 June 10 |  |
| Design essentially complete | 31 May | No forecast date | No forecast date |

    - A spread sheet of all the pending drawing issues noted here is being consolidated; these issues will be captured for both sites.

10.11.2 After review of the duct bank drawings EDG needs to perform an evaluation the dimensions shown they do not reconcile with depths mentioned in discussions.  IF all is equal to drawings there is no room for piping to cross over duct banks.  The handhold elevation will not cover 4” 36” radius 90 degree turns in conduit.

  - ISSUED DRAWINGS:

11. PICTURES:

Photo 1: Site after rains

Photo 2: Oily water excavation

Photo 3: 7EA PEECC ready to pour